## Frese S
QUICK - CALC Frese S
Setting & Selection program
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 1200 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp (kPa) | Pre-set | Kv | Min. ∆P (kPa)
DN15 LP | 25-804 | 8-250 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN15 HP | 40-1100 | 16-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 LP | 41-1265 | 9-250 | 9.0101 | 3.1677 | 14.3508
DN20 HP | 66-1850 | 12-400 | 6.7839 | 2.6336 | 20.7622
DN25 LP | 61-1663 | 9-250 | 6.4402 | 3.1622 | 14.4003
DN25 HP | 89-2350 | 12-400 | 4.8698 | 2.7192 | 19.4744
DN32 | 217-4800 | 14-400 | 2.9228 | 2.8834 | 17.3203
DN40 | 175-7450 | 15-400 | 2.4488 | 2.9042 | 17.0726
DN50 | 440-10350 | 17-400 | 1.6696 | 2.809 | 18.2498
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 LP | [5 empty] | 2.2 | 25 | 804 | UDEN FOR OMRÅDET | 20
DN15 HP | [5 empty] | 2.4 | 40 | 1100 | UDEN FOR OMRÅDET | 20
DN20 LP | [5 empty] | 3.3 | 41 | 1265 | 1200 | 20
DN20 HP | [5 empty] | 3.6 | 66 | 1850 | 1200 | 20
DN25 LP | [5 empty] | 4.1 | 61 | 1663 | 1200 | 20
DN25 HP | [5 empty] | 4.4 | 89 | 2350 | 1200 | 20
DN32 | [5 empty] | 8.8 | 217 | 4800 | 1200 | 20
DN40 | [5 empty] | 13.2 | 175 | 7450 | 1200 | 20
DN50 | [5 empty] | 16.7 | 440 | 10350 | 1200 | 20
OBSOLETE PRODUCT

## SIGMA Compact
QUICK - CALC SIGMA Compact
Setting & Selection program
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 1500 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp (kPa) | Pre-set | Kv | Min. ∆P (kPa)
DN15 Low | 40-900 | 10-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN15 High | 60-1080 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 Low | 86-1550 | 9-400 | 3.569 | 1.196 | 13.526
DN20 High | 102-1930 | 16-400 | 2.8 | 0.92688 | 18.352
DN25 Low | 95-2000 | 10-400 | 2.9 |  | 20.72
DN25 High | 137-2400 | 14-400 | 2.4 | 1.0696 | 17.1032
DN25L (53-2204 withdrawn) | 150-1930 | 17-400 | 2.9996 | 1.4841 | 11.8079
DN32 | 200-5000 | 15-400 | 1.3716 | 1.0133 | 15.832
DN40 | 719-7400 | 10-400 | 0.94385 | 0.39399 | 10
DN50 | 900-10350 | 10-400 | 0.8 | 0.53997 | 10
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 LF | [5 empty] | 2.6 | 40 | 900 | UDEN FOR OMRÅDET | 20
DN15 HF | [5 empty] | 2.6 | 60 | 1080 | UDEN FOR OMRÅDET | 20
DN20 LF | [5 empty] | 4 | 86 | 1550 | 1500 | 20
DN20 HF | [5 empty] | 4 | 102 | 1930 | 1500 | 20
DN25 LF | [5 empty] | 3.9 | 95 | 2000 | 1500 | 20
DN25 HF | [5 empty] | 4.2 | 137 | 2400 | 1500 | 20
DN25L (53-2204 withdrawn) | [5 empty] | 5.4 | 150 | 1930 | 1500 | 20
DN32 | [5 empty] | 10.9 | 200 | 5000 | 1500 | 20
DN40 | [5 empty] | 18 | 719 | 7400 | 1500 | 20
DN50 | [5 empty] | 20.3 | 900 | 10350 | 1500 | 20

## SIGMA Compact Flange
QUICK - CALC SIGMA Compact Flanged
Setting & Selection program
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 90 | (m3/h) Flow
Dimension & Type | Range |  | Calculation
| Flow (m3/h) | Range ∆Pp(kPa) | Pre-set | Min. ∆P (kPa)
DN50 Ultra High Flow | 1.40-11.50 | 11-800 | NOT POSSIBLE | NOT POSSIBLE
DN50 Standard Low Flow | 2.48-15.00 | 7-800 | NOT POSSIBLE | NOT POSSIBLE
DN50 Standard High Flow | 3.92-24.00 | 19-800 | NOT POSSIBLE | NOT POSSIBLE
DN65 Ultra Low Flow | 2.48-15.00 | 7-800 | -396.4947 | NOT POSSIBLE
DN65 Ultra High Flow | 4.20-24.00 | 19-800 | NOT POSSIBLE | NOT POSSIBLE
DN65 Standard Low Flow | 4.38-25.00 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN65 Standard High Flow | 5.95-35.00 | 30-800 | NOT POSSIBLE | NOT POSSIBLE
DN80 Ultra Low Flow | 4.38-25.00 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN80 Ultra High Flow | 5.95-35.00 | 30-800 | NOT POSSIBLE | NOT POSSIBLE
DN80 Standard Low Flow | 5.34-34.00 | 16-800 | NOT POSSIBLE | NOT POSSIBLE
DN80 Standard High Flow | 7.02-43.00 | 23-800 | NOT POSSIBLE | NOT POSSIBLE
DN100 Ultra Low Flow | 5.34-34.00 | 16-800 | NOT POSSIBLE | NOT POSSIBLE
DN100 Ultra High Flow | 7.02-43.00 | 23-800 | NOT POSSIBLE | NOT POSSIBLE
DN100 Standard Low Flow | 12.10-68.00 | 20-800 | NOT POSSIBLE | NOT POSSIBLE
DN100 Standard High Flow | 14.80-90.00 | 30-800 | 4.0105 | 74.9612
DN125 Ultra Low Flow | 12.10-68.00 | 20-800 | NOT POSSIBLE | NOT POSSIBLE
DN125 Ultra High Flow | 14.80-90.00 | 30-800 | 4.0105 | 74.9612
DN125 Standard Low Flow | 18.5-110.0 | 16-800 | 3.5107 | 25.0704
DN125 Standard High Flow | 23.0-135.0 | 27-800 | 2.8631 | 32.1154
DN150 Standard Low Flow | 25.6-148.0 | 21-800 | 2.5901 | 26.5154
DN150 Standard High Flow | 32.0-195.0 | 33-800 | 2.0229 | 34.1669
DN200 Standard Low Flow | 95.0-210.0 | 11-800 | NOT POSSIBLE | NOT POSSIBLE
DN200 Standard High Flow | 130.0-280.0 | 31-800 | NOT POSSIBLE | NOT POSSIBLE
DN250 Standard Low Flow | 190.0-475.0 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN250 Standard High Flow | 245.0-600.0 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN300 Standard Low Flow | 190.0-475.0 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN300 Standard High Flow | 245.0-600.0 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Z | Kvs | Min | Max | Evaluering af Flow
DN50 Ultra High Flow |  |  |  |  | 19.2 | 1.4 | 11.5 | UDEN FOR OMRÅDET
DN50 Standard Low Flow |  |  |  |  | 33.5 | 2.48 | 15 | UDEN FOR OMRÅDET
DN50 Standard High Flow |  |  |  |  | 33.5 | 3.92 | 24 | UDEN FOR OMRÅDET
DN65 Ultra Low Flow |  |  |  |  | 33.5 | 2.48 | 15 | UDEN FOR OMRÅDET
DN65 Ultra High Flow |  |  |  |  | 33.5 | 4.2 | 24 | UDEN FOR OMRÅDET
DN65 Standard Low Flow |  |  |  |  | 50 | 4.38 | 25 | UDEN FOR OMRÅDET
DN65 Standard High Flow |  |  |  |  | 50 | 5.95 | 35 | UDEN FOR OMRÅDET
DN80 Ultra Low Flow |  |  |  |  | 50 | 4.38 | 25 | UDEN FOR OMRÅDET
DN80 Ultra High Flow |  |  |  |  | 50 | 5.95 | 35 | UDEN FOR OMRÅDET
DN80 Standard Low Flow |  |  |  |  | 68 | 5.3 | 34 | UDEN FOR OMRÅDET
DN80 Standard High Flow |  |  |  |  | 68 | 7 | 43 | UDEN FOR OMRÅDET
DN100 Ultra Low Flow |  |  |  |  | 68 | 5.34 | 34 | UDEN FOR OMRÅDET
DN100 Ultra High Flow |  |  |  |  | 68 | 7.02 | 43 | UDEN FOR OMRÅDET
DN100 Standard Low Flow |  |  |  |  | 115 | 12.1 | 68 | UDEN FOR OMRÅDET
DN100 Standard High Flow |  |  |  |  | 115 | 14.8 | 90 | 90
DN125 Ultra Low Flow |  |  |  |  | 115 | 12.1 | 68 | UDEN FOR OMRÅDET
DN125 Ultra High Flow |  |  |  |  | 115 | 14.8 | 90 | 90
DN125 Standard Low Flow |  |  |  |  | 167 | 18.5 | 110 | 90
DN125 Standard High Flow |  |  |  |  | 167 | 23 | 135 | 90
DN150 Standard Low Flow |  |  |  |  | 250 | 25.6 | 148 | 90
DN150 Standard High Flow |  |  |  |  | 241.9 | 32 | 195 | 90
DN200 Standard Low Flow |  |  |  |  | 371 | 95 | 210 | UDEN FOR OMRÅDET
DN200 Standard High Flow |  |  |  |  | 317 | 130 | 280 | UDEN FOR OMRÅDET
DN250 Standard Low Flow |  |  |  |  | 840 | 190 | 475 | UDEN FOR OMRÅDET
DN250 Standard High Flow |  |  |  |  | 717 | 245 | 600 | UDEN FOR OMRÅDET
DN300 Standard Low Flow |  |  |  |  | 840 | 190 | 475 | UDEN FOR OMRÅDET
DN300 Standard High Flow |  |  |  |  | 717 | 245 | 600 | UDEN FOR OMRÅDET

## Frese OPTIMA
QUICK - CALC Frese OPTIMA
Setting & Selection program
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 2204 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp(kPa) | Pre-set | Kv | Min. ∆P (kPa)
DN15 LF | 78-625 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN15 HF | 244-1724 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 LF | 131-1050 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 HF | 292-2039 | 13-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN25 LF | 231-1722 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN25 HF | 292-2039 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN32 | 465-3056 | 14-400 | 2.464 | 5.4061 | 16.6207
DN40 | 2022-7105 | 16-400 | 0.54367 | 5.421 | 16.5296
DN50 | 2204-8586 | 19-400 | 0.51234 | 5.2201 | 19
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 LF | [5 empty] | 1.6 | 78 | 625 | UDEN FOR OMRÅDET | 20
DN15 HF | [5 empty] | 4.1 | 244 | 1724 | UDEN FOR OMRÅDET | 20
DN20 LF | [5 empty] | 2.6 | 131 | 1050 | UDEN FOR OMRÅDET | 20
DN20 HF | [5 empty] | 4.3 | 292 | 2039 | UDEN FOR OMRÅDET | 20
DN25 LF | [5 empty] | 4.3 | 231 | 1722 | UDEN FOR OMRÅDET | 20
DN25 HF | [5 empty] | 4.3 | 292 | 2039 | UDEN FOR OMRÅDET | 20
DN32 | [5 empty] | 7.2 | 465 | 3056 | 2204 | 20
DN40 | [5 empty] | 13.9 | 2022 | 7105 | 2204 | 20
DN50 | [5 empty] | 15.2 | 2204 | 8586 | 2204 | 20
OBSOLETE PRODUCT

## OPTIMA Compact
QUICK - CALC OPTIMA Compact & OPTIMA Compact Veriflow
Setting & Selection program
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 5000 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp(kPa) | Pre-set | Min. ∆P (kPa)
DN10 Low 2,5 | 30-200 | 14-800 | NOT POSSIBLE | NOT POSSIBLE
DN10 Low 5,0 | 65-370 | 14-800 | NOT POSSIBLE | NOT POSSIBLE
DN15 Low 2,5 | 30-200 | 14-800 | NOT POSSIBLE | NOT POSSIBLE
DN15 Low 5,0 | 65-370 | 14-800 | NOT POSSIBLE | NOT POSSIBLE
DN15 High 2,5 | 100-575 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN15 High 5,0 | 220-1330 | 16-800 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 2,5 | 100-575 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 4,0 * | 160-990 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 5,0 | 220-1330 | 16-800 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 5,5 | 300-1800 | 18-800 | NOT POSSIBLE | NOT POSSIBLE
DN25 Low 5,5 | 280-1800 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN25L High 5,5 | 600-3609 | 17-800 | NOT POSSIBLE | NOT POSSIBLE
DN32 | 550-4001 | 18-800 | NOT POSSIBLE | NOT POSSIBLE
DN40 | 1370-9500 | 10-800 | 2.4595 | 12.848
DN50 | 1400-11500 | 10-800 | 2.3028 | 14.994
*) Not standard product
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
Type |  |  | X | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN10 Low 2,5 |  |  |  |  | 0.5 | 30 | 200 | UDEN FOR OMRÅDET | 20
DN10 Low 5,0 |  |  |  |  | 0.9 | 65 | 370 | UDEN FOR OMRÅDET | 20
DN15 Low 2,5 |  |  |  |  | 0.5 | 30 | 200 | UDEN FOR OMRÅDET | 20
DN15 Low 5,0 |  |  |  |  | 0.9 | 65 | 370 | UDEN FOR OMRÅDET | 20
DN15 High 2,5 |  |  |  |  | 1.3 | 100 | 575 | UDEN FOR OMRÅDET | 20
DN15 High 5,0 |  |  |  |  | 2.7 | 220 | 1330 | UDEN FOR OMRÅDET | 20
DN20 High 2,5 |  |  |  |  | 1.3 | 100 | 575 | UDEN FOR OMRÅDET | 20
DN20 High 4,0 |  |  |  |  | 2.1 | 160 | 990 | UDEN FOR OMRÅDET | 20
DN20 High 5,0 |  |  |  |  | 2.7 | 220 | 1330 | UDEN FOR OMRÅDET | 20
DN20 High 5,5 |  |  |  |  | 2.9 | 300 | 1800 | UDEN FOR OMRÅDET | 20
DN25 Low 5,5 |  |  |  |  | 2.9 | 280 | 1800 | UDEN FOR OMRÅDET | 20
DN25L High 5,5 |  |  |  |  | 7.5 | 600 | 3609 | UDEN FOR OMRÅDET | 20
DN32 |  |  |  |  | 7.6 | 550 | 4001 | UDEN FOR OMRÅDET | 20
DN40 |  |  |  |  | 19 | 1370 | 9500 | 5000 | 20
DN50 |  |  |  |  | 19 | 1400 | 11500 | 5000 | 20

## OPTIMA Compact Flanged
QUICK - CALC OPTIMA Compact & OPTIMA Compact Veriflow
Setting & Selection program
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 30 | (m3/h) Flow
Dimension & Type | Range |  | Calculation
| Flow (m3/h) | Range ∆Pp(kPa) | Pre-set | Min. ∆P (kPa)
DN50 Ultra High Flow | 1.40-11.5 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN50 Standard Low Flow | 2.50-15.0 | 7-800 | NOT POSSIBLE | NOT POSSIBLE
DN50 Standard High Flow | 3.90-24.0 | 19-800 | NOT POSSIBLE | NOT POSSIBLE
DN65 Ultra Low Flow | 3.00-16.0 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN65 Ultra High Flow | 4.20-24.0 | 19-800 | NOT POSSIBLE | NOT POSSIBLE
DN65 Standard Low Flow | 4.40-25.0 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN65 Standard High Flow | 6.00-35.0 | 30-800 | 3.5778 | 43.4554
DN80 Ultra Low Flow | 4.40-25.0 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN80 Ultra High Flow | 6.00-35.0 | 30-800 | 3.5713 | 41.7751
DN80 Standard Low Flow | 5.30-34.0 | 16-800 | 3.7336 | 23.2053
DN80 Standard High Flow | 7.00-43.0 | 23-800 | 3.0625 | 30.9831
DN100 Ultra Low Flow | 5.30-34.0 | 16-800 | 3.6971 | 23.3128
DN100 Ultra High Flow | 7.00-43.0 | 23-800 | 3.0654 | 22.1834
DN100 Standard Low Flow | 12.1-68.0 | 20-800 | 1.9903 | 21.9913
DN100 Standard High Flow | 14.8-90.0 | 30-800 | 1.4685 | 32.0436
DN125 Ultra Low Flow | 12.1-68.0 | 20-800 | 1.9937 | 21.9992
DN125 Ultra High Flow | 14.8-90.0 | 30-800 | 1.4668 | 22
DN125 Standard Low Flow | 18.5-110 | 16-800 | 1.0626 | 16.1696
DN125 Standard High Flow | 23.0-135 | 27-800 | 0.79482 | 27
DN150 Standard Low Flow | 25.6-148 | 21-800 | 0.72397 | 21
DN150 Standard High Flow | 32.0-195 | 33-800 | NOT POSSIBLE | NOT POSSIBLE
DN200 Standard Low Flow | 95.0-210 | 11-800 | NOT POSSIBLE | NOT POSSIBLE
DN200 Standard High Flow | 130-280 | 31-800 | NOT POSSIBLE | NOT POSSIBLE
DN250 Standard Low Flow | 190-475 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN250 Standard High Flow | 245-600 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
DN300 Standard Low Flow | 190-475 | 10-800 | NOT POSSIBLE | NOT POSSIBLE
DN300 Standard High Flow | 245-600 | 15-800 | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Z | Kvs | Min | Max | Evaluering af Flow
DN50 Ultra High Flow |  |  |  |  | 19.2 | 1.4 | 11.5 | UDEN FOR OMRÅDET
DN50 Standard Low Flow |  |  |  |  | 33.5 | 2.5 | 15 | UDEN FOR OMRÅDET
DN50 Standard High Flow |  |  |  |  | 33.5 | 3.9 | 24 | UDEN FOR OMRÅDET
DN65 Ultra Low Flow |  |  |  |  | 33.5 | 3 | 16 | UDEN FOR OMRÅDET
DN65 Ultra High Flow |  |  |  |  | 33.5 | 4.2 | 24 | UDEN FOR OMRÅDET
DN65 Standard Low Flow |  |  |  |  | 50 | 4.4 | 25 | UDEN FOR OMRÅDET
DN65 Standard High Flow |  |  |  |  | 50 | 6 | 35 | 30
DN80 Ultra Low Flow |  |  |  |  | 50 | 4.4 | 25 | UDEN FOR OMRÅDET
DN80 Ultra High Flow |  |  |  |  | 50 | 6 | 35 | 30
DN80 Standard Low Flow |  |  |  |  | 68 | 5.3 | 34 | 30
DN80 Standard High Flow |  |  |  |  | 68 | 7 | 43 | 30
DN100 Ultra Low Flow |  |  |  |  | 68 | 5.3 | 34 | 30
DN100 Ultra High Flow |  |  |  |  | 68 | 7 | 43 | 30
DN100 Standard Low Flow |  |  |  |  | 115 | 12.1 | 68 | 30
DN100 Standard High Flow |  |  |  |  | 115 | 14.8 | 90 | 30
DN125 Ultra Low Flow |  |  |  |  | 115 | 12.1 | 68 | 30
DN125 Ultra High Flow |  |  |  |  | 115 | 14.8 | 90 | 30
DN125 Standard Low Flow |  |  |  |  | 167 | 18.5 | 110 | 30
DN125 Standard High Flow |  |  |  |  | 167 | 23 | 135 | 30
DN150 Standard Low Flow |  |  |  |  | 250 | 25.6 | 148 | 30
DN150 Standard High Flow |  |  |  |  | 241.9 | 32 | 195 | UDEN FOR OMRÅDET
DN200 Standard Low Flow |  |  |  |  | 371 | 95 | 210 | UDEN FOR OMRÅDET
DN200 Standard High Flow |  |  |  |  | 317 | 130 | 280 | UDEN FOR OMRÅDET
DN250 Standard Low Flow |  |  |  |  | 840 | 190 | 475 | UDEN FOR OMRÅDET
DN250 Standard High Flow |  |  |  |  | 717 | 245 | 600 | UDEN FOR OMRÅDET
DN300 Standard Low Flow |  |  |  |  | 840 | 190 | 475 | UDEN FOR OMRÅDET
DN300 Standard High Flow |  |  |  |  | 717 | 245 | 600 | UDEN FOR OMRÅDET

## Frese PV
QUICK - CALC Frese PV
Setting & Selection program
Input
Input ∆Ps = |  | 40 | (kPa) Differential Pessure setting
Input Q = |  | 15000 | (l/h) Design flow
Dim. | ∆Ps range | Range |  | Pre-set
|  | Flow (l/h) | Range ∆Pp (kPa) | Number of turns
DN15 | 5-30 kPa | 50-600 | 5-400 | NOT POSSIBLE
DN15 | 20-60 kPa | 100-1200 | 20-400 | NOT POSSIBLE
DN20 | 5-30kPa | 100-1000 | 5-400 | NOT POSSIBLE
DN20 | 20-60kPa | 150-2000 | 20-400 | NOT POSSIBLE
DN25 | 5-30 kPa | 600-2500 | 5-400 | NOT POSSIBLE
DN25 | 20-60 kPa | 700-4000 | 20-400 | NOT POSSIBLE
DN32 | 20-80 kPa | 1000-5000 | 20-400 | NOT POSSIBLE
DN40 | 20-80 kPa | 3000-8000 | 20-400 | NOT POSSIBLE
DN50 | 20-80 kPa | 5000-15000 | 20-400 | 13.3532
Calculation of pressure loss
Dimension |  | ∆Pv (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN15 20-60 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN20 5-30kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN20 20-60kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN25 5-30 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN25 20-60 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN32 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN40 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN50 20-80 kPa |  | 70.2225 | 110.2225
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa |  | 5 | 494.76 | 0.5575 | 3.6 | 50 | 600 | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET
DN15 20-60 kPa |  | 20 | 747.59 | 0.3133 | 3.6 | 100 | 1200 | UDEN FOR OMRÅDET | 40
DN20 5-30 kPa |  | 5 | 682.82 | 0.59 | 4 | 100 | 1000 | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET
DN20 20-60 kPa |  | 20 | 596.44 | 0.324 | 4 | 150 | 2000 | UDEN FOR OMRÅDET | 40
DN25 5-30 kPa |  | 5 | 802.65 | 1.26 | 9.5 | 600 | 2500 | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET
DN25 20-60 kPa |  | 20 | 1529.6 | 0.7175 | 9.5 | 700 | 4200 | UDEN FOR OMRÅDET | 40
DN32 20-80 kPa |  | 20 | 1338.84 | 0.4833 | 11.4 | 1000 | 5000 | UDEN FOR OMRÅDET | 40
DN40 20-80 kPa |  | 20 | 2213.08 | 0.4133 | 16.4 | 3000 | 8000 | UDEN FOR OMRÅDET | 40
DN50 20-80 kPa |  | 20 | 2234.42 | 0.352 | 17.9 | 5000 | 15000 | 15000 | 40
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve
OBSOLETE PRODUCT

## PV Compact
QUICK - CALC Frese PV Compact
Setting & Selection program
Input
Input ∆Ps = |  | 20 | (kPa) Differential Pessure setting
Input Q = |  | 500 | (l/h) Design flow
Dim. | ∆Ps range | Range |  | Pre-set
|  | Flow (l/h) | Range ∆Pp (kPa) | Number of turns
DN15 | 5-30 kPa | 50-600 | 5-450 | 11.8382
DN15 | 20-60 kPa | 100-1000 | 20-450 | 1.3
DN20 | 5-30 kPa | 100-1000 | 5-450 | 11.8382
DN20 | 20-60 kPa | 150-2000 | 20-450 | 1.2974
DN25 | 5-30 kPa | 600-2100 | 5-450 | NOT POSSIBLE
DN25L | 20-80 kPa | 750-4200 | 20-450 | NOT POSSIBLE
DN32 | 20-80 kPa | 1000-5000 | 20-450 | NOT POSSIBLE
DN40 | 20-80 kPa | 3000-8000 | 20-450 | NOT POSSIBLE
DN50 | 20-80 kPa | 5000-11500 | 20-450 | NOT POSSIBLE
DN50 Ultra | 20-80 kPa | 3200-13000 | 20-450 | NOT POSSIBLE
Calculation of pressure loss
Dimension |  | ∆Pv (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa |  | 2.9727 | 22.9727
DN15 20-60 kPa |  | 2.9727 | 22.9727
DN20 5-30 kPa |  | 2.0408 | 22.0408
DN20 20-60 kPa |  | 2.0408 | 22.0408
DN25 5-30 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN25 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN32 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN40 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN50 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN50 Ultra 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa |  | 5 | 272 | 0.68 | 2.9 | 50 | 600 | 500 | 20
DN15 20-60 kPa |  | 20 | 312.5 | 0.4015 | 2.9 | 100 | 1000 | 500 | 20
DN20 5-30 kPa |  | 5 | 272 | 0.68 | 3.5 | 100 | 1000 | 500 | 20
DN20 20-60 kPa |  | 20 | 313 | 0.402 | 3.5 | 150 | 2000 | 500 | 20
DN25 5-30 kPa |  | 5 | 322 | 0.612 | 4 | 600 | 2100 | UDEN FOR OMRÅDET | 20
DN25 20-80 kPa |  | 20 | 1180 | 0.285 | 8.7 | 750 | 4200 | UDEN FOR OMRÅDET | 20
DN32 20-80 kPa |  | 20 | 1201 | 0.275 | 10.1 | 1000 | 5000 | UDEN FOR OMRÅDET | 20
DN40 20-80 kPa |  | 20 | 2411 | 0.299 | 15.8 | 3000 | 8000 | UDEN FOR OMRÅDET | 20
DN50 20-80 kPa |  | 20 | 1547 | 0.23 | 16.2 | 5000 | 11500 | UDEN FOR OMRÅDET | 20
DN50 Ultra 20-80 kPa |  | 12.5 | 2029 | 0.22 | 18.6 | 3200 | 13000 | UDEN FOR OMRÅDET | 20
|  | Offset | Flow/omdr | DP/omdr
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve

## Frese PVS
QUICK - CALC Frese PVS | [9 empty] | QUICK - CALC Frese S
Setting & Selection program | [9 empty] | Auslegungsprogramm für Frese S Dynamischer Volumenstromregler
| Input | [9 empty] | Eingabe
Input ∆Ps = | 10 | (kPa) Differential pressure setting | [7 empty] | Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 1200 | (l/h) Design flow in Zone | [7 empty] | Eingabe Q = | 25 | (l/h) Auslegungsvolumenstrom | (L/h) Auslegungsvolumenstrom
Frese PV (Return) |  | Frese S (Supply) |  |  |  | PVS System
Pre-set Frese PV |  | Pre-set Frese S |  |  |  | Total Pressure loss
Dimension | Number of turns | Dimension | Pre-set | Kv | Min. ∆P (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa | NOT POSSIBLE | DN15 LP | NOT POSSIBLE | #VALUE! | NICHT MÖGLICH | NOT POSSIBLE
DN15 20-60 kPa | NOT POSSIBLE | DN15 HP | NOT POSSIBLE | #VALUE! | NICHT MÖGLICH | NOT POSSIBLE
DN20 5-30kPa | NOT POSSIBLE | DN20 LP | 9.0101 | 3.1677 | 14.3508 | NOT POSSIBLE
DN20 20-60kPa | NOT POSSIBLE | DN20 HP | 6.7839 | 2.6336 | 20.7622 | NOT POSSIBLE
DN25 5-30 kPa | 8.995 | DN25 LP | 6.4402 | 3.1622 | 14.4003 | 25.9959
DN25 20-60 kPa | NOT POSSIBLE | DN25 HP | 4.8698 | 2.7192 | 19.4744 | NOT POSSIBLE
DN32 20-80 kPa | NOT POSSIBLE | DN32 HP | 2.9228 | 2.8834 | 17.3203 | NOT POSSIBLE
DN40 20-80 kPa | NOT POSSIBLE | DN40 HP | 2.4488 | 2.9042 | 17.0726 | NOT POSSIBLE
DN50 20-80 kPa | NOT POSSIBLE | DN50 HP | 1.6696 | 2.809 | 18.2498 | NOT POSSIBLE
∆Pv (kPa)
NOT POSSIBLE
NOT POSSIBLE
1.5956
NOT POSSIBLE
NOT POSSIBLE
NOT POSSIBLE
2
Dim. ∆Ps Rang. | Frese PV ∆P - Controller |  | Frese S Flow Controller |  |  |  | Frese PV&S ∆P & Flow Controller
| Flow range (l/h) | ∆Pp range (kPa) | Flow range (l/h) |  |  | ∆Pp range (kPa) | ∆Ps range (kPa) | Flow range (l/h) | ∆Pp range (kPa)
DN15 5-30kPa | 50-600 | 5-400 | 25-804 |  |  | 8-250 | 5-30 | 50-600 | 14-250
DN15 20-60kPa | 100-1200 | 20-400 | 40-1100 |  |  | 16-400 | 20-60 | 100-1100 | 37-400
DN20 5-30 kPa | 100-1000 | 5-400 | 41-1265 |  |  | 9-250 | 5-30 | 100-1000 | 14-250
DN20 20-60kPa | 150-2000 | 20-400 | 66-1850 |  |  | 12-400 | 20-60 | 150-1850 | 33-400
DN25 5-30kPa | 600-2500 | 5-400 | 61-1663 |  |  | 9-250 | 5-30 | 600-1663 | 17-250
DN25 20-60kPa | 700-4000 | 20-400 | 89-2350 |  |  | 12-400 | 20-60 | 700-2350 | 37-400
DN32 20-80kPa | 1000-5000 | 20-400 | 217-4800 |  |  | 14-400 | 20-80 | 1000-4800 | 38-400
DN40 20-80kPa | 3000-8000 | 20-400 | 175-7450 |  |  | 15-400 | 20-80 | 3000-7450 | 45-400
DN50 20-80kPa | 5000-15000 | 20-400 | 440-10350 |  |  | 17-400 | 20-80 | 5000-10350 | 57-400 | Der Regelbereich ist definiert von Min. Pumpendruck (Min. ∆Pp) bis Max. Pumpendruck (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN | [9 empty] | ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type | X | Y | Z | Kvs | Min | Max |  | Evaluering af Flow | Evaluering af Dp | Type | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa | 5 | 494.76 | 0.5575 | 3.6 | 50 | 600 |  | UDEN FOR OMRÅDET | 10 | DN15 LP |  |  |  | 2.2 | 25 | 804 | UDEN FOR OMRÅDET | 20
DN15 20-60 kPa | 20 | 747.59 | 0.3133 | 3.6 | 100 | 1200 |  | 1200 | UDEN FOR OMRÅDET | DN15 HP |  |  |  | 2.4 | 40 | 1100 | UDEN FOR OMRÅDET | 20
DN20 5-30 kPa | 5 | 682.82 | 0.59 | 4 | 100 | 1000 |  | UDEN FOR OMRÅDET | 10 | DN20 LP |  |  |  | 3.3 | 41 | 1265 | 1200 | 20
DN20 20-60 kPa | 20 | 596.44 | 0.324 | 4 | 150 | 2000 |  | 1200 | UDEN FOR OMRÅDET | DN20 HP |  |  |  | 3.6 | 66 | 1850 | 1200 | 20
DN25 5-30 kPa | 5 | 802.65 | 1.26 | 9.5 | 600 | 2500 |  | 1200 | 10 | DN25 LP |  |  |  | 4.1 | 61 | 1663 | 1200 | 20
DN25 20-60 kPa | 20 | 1529.6 | 0.7175 | 9.5 | 700 | 4200 |  | 1200 | UDEN FOR OMRÅDET | DN25 HP |  |  |  | 4.4 | 89 | 2350 | 1200 | 20
DN32 20-80 kPa | 20 | 1338.84 | 0.4833 | 11.4 | 1000 | 4800 |  | 1200 | UDEN FOR OMRÅDET | DN32 |  |  |  | 8.8 | 217 | 4800 | 1200 | 20
DN40 20-80 kPa | 20 | 2213.08 | 0.4133 | 16.4 | 3000 | 7450 |  | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET | DN40 |  |  |  | 13.2 | 175 | 7450 | 1200 | 20
DN50 20-80 kPa | 20 | 2234.42 | 0.352 | 17.9 | 5000 | 10350 |  | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET | DN50 |  |  |  | 16.7 | 440 | 10350 | 1200 | 20
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve
S
PV
Frese S (Supply)
Frese PV (Return)
Frese PV
Frese S
OBSOLETE PRODUCT

## PV-SIGMA
QUICK - CALC PV-SIGMA Compact | [9 empty] | QUICK - CALC Frese S
Setting & Selection program | [9 empty] | Auslegungsprogramm für Frese S Dynamischer Volumenstromregler
| Input | [9 empty] | Eingabe
Input ∆Ps = | 30 | (kPa) Differential pressure in system | [7 empty] | Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 1300 | (l/h) Design flow in system | [7 empty] | Eingabe Q = | 25 | (l/h) Auslegungsvolumenstrom | (L/h) Auslegungsvolumenstrom
PV Compact (Return) |  | SIGMA Compact (Supply) |  |  |  | PV-SIGMA System
Pre-set PV Compact |  | Pre-set SIGMA Compact |  |  |  | Total pressure loss
Dimension | Number of turns | Dimension | Pre-set |  | Min. ∆P (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa | NOT POSSIBLE | DN15 Low | NOT POSSIBLE |  | #VALUE! | NOT POSSIBLE
DN15 20-60 kPa | NOT POSSIBLE | DN15 High | NOT POSSIBLE |  | #VALUE! | NOT POSSIBLE
DN20 5-30kPa | NOT POSSIBLE | DN20 Low | 2.8416 |  | 11.5 | NOT POSSIBLE
DN20 20-60kPa | 7.8734 | DN20 High | 2.3 |  | 16.7 | 60.4959
DN25 5-30 kPa | 17.4435 | DN25 High | 2.1 |  | 15.6 | 56.1625
DN25 20-80 kPa | 3.3017 | DN25 High | 2.1 |  | 15.6 | 47.8328
DN32 20-80 kPa | 2.9624 | DN32 | 1.2358 |  | 15.7 | 47.3567
DN40 20-80 kPa | NOT POSSIBLE | DN40 | 0.82826 |  | 10 | NOT POSSIBLE
DN50 20-80 kPa | NOT POSSIBLE | DN50 | 0.7 |  | 10 | NOT POSSIBLE
∆P-PV (kPa)
NOT POSSIBLE
NOT POSSIBLE
NOT POSSIBLE
13.7959
10.5625
2.2328
1.6567
NOT POSSIBLE
NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
| PV Compact ∆P - Controller |  | SIGMA Compact Flow Controller |  |  |  | PV-SIGMA Compact System ∆P & Flow controller
Dim. ∆Ps Range | Flow range (l/h) | ∆Pp range (kPa) | Flow range (l/h) |  |  | ∆Pp range (kPa) | ∆Ps range (kPa) | Flow range (l/h) | ∆Pp range (kPa)
DN15 5-30kPa | 50-600 | 7-450 | 40-900 |  |  | 10-400 | 5-30 | 50-600 | 10-400
DN15 20-60kPa | 100-1000 | 22-450 | 60-1080 |  |  | 14-400 | 20-60 | 100-1000 | 22-400
DN20 5-30 kPa | 100-1000 | 7-450 | 86-1550 |  |  | 9-400 | 5-30 | 100-1000 | 9-400
DN20 20-60 kPa | 150-2000 | 22-450 | 102-1930 |  |  | 16-400 | 20-60 | 150-1930 | 22-400
DN25 5-30kPa | 600-2100 | 7-450 | 137-2400 |  |  | 14-400 | 5-30 | 600-2100 | 14-400
DN25 20-80kPa | 750-4200 | 22-450 | 137-2400 |  |  | 14-400 | 20-80 | 750-2400 | 22-400
DN32 20-80kPa | 1000-5000 | 22-450 | 200-5000 |  |  | 15-400 | 20-80 | 1000-5000 | 22-400
DN40 20-80kPa | 3000-8000 | 22-450 | 719-7400 |  |  | 10-400 | 20-80 | 3000-7400 | 22-400
DN50 20-80kPa | 5000-11500 | 22-450 | 900-10350 |  |  | 10-400 | 20-80 | 5000-10350 | 22-400 | Der Regelbereich ist definiert von Min. Pumpendruck (Min. ∆Pp) bis Max. Pumpendruck (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN | [9 empty] | ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  | X (min Kpa) | Y (Flow/Omdr) | Z (Omdr/kpa) | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp | Type | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa |  | 5 | 272 | 0.68 | 2.9 | 50 | 600 | UDEN FOR OMRÅDET | 30 | DN15 LF |  |  |  | 2.6 | 40 | 900 | UDEN FOR OMRÅDET | 30
DN15 20-60 kPa |  | 20 | 312.5 | 0.4015 | 2.9 | 100 | 1000 | UDEN FOR OMRÅDET | 30 | DN15 HF |  |  |  | 2.6 | 60 | 1080 | UDEN FOR OMRÅDET | 30
DN20 5-30 kPa |  | 5 | 272 | 0.68 | 3.5 | 100 | 1000 | UDEN FOR OMRÅDET | 30 | DN20 LF |  |  |  | 4 | 86 | 1550 | 1300 | 30
DN20 20-60 kPa |  | 20 | 313 | 0.402 | 3.5 | 150 | 2000 | 1300 | 30 | DN20 HF |  |  |  | 4 | 102 | 1930 | 1300 | 30
DN25 5-30 kPa |  | 5 | 321.5 | 0.612 | 4 | 600 | 2100 | 1300 | 30 | DN25 HF |  |  |  | 4.2 | 137 | 2400 | 1300 | 30
DN25 20-80 kPa |  | 20 | 1180 | 0.285 | 8.7 | 750 | 4200 | 1300 | 30 | DN25 HF |  |  |  | 4.2 | 137 | 2400 | 1300 | 30
DN32 20-80 kPa |  | 20 | 1201 | 0.275 | 10.1 | 1000 | 5000 | 1300 | 30 | DN32 |  |  |  | 10.9 | 200 | 5000 | 1300 | 30
DN40 20-80 kPa |  | 20 | 2410.7 | 0.2988 | 15.8 | 3000 | 8000 | UDEN FOR OMRÅDET | 30 | DN40 |  |  |  | 18 | 719 | 7400 | 1300 | 30
DN50 20-80 kPa |  | 20 | 1547 | 0.23 | 16.2 | 5000 | 11500 | UDEN FOR OMRÅDET | 30 | DN50 |  |  |  | 20.3 | 900 | 10350 | 1300 | 30
∆Pp = Pump pressure
∆Ps = Differential pressure in system
∆Pv = Pressure loss across valve
Frese SIGMA Compact (Supply)
Frese PV Compact (Return)
Frese PV Compact
Frese SIGMA Compact
∆Pv
∆Pv
∆Ps
∆Pp
∆Pp = ∆Ps + ∆Pv

## OPTIMA P Compact
QUICK - CALC OPTIMA P Compact
Setting & Selection program
Input
| Input Q: | 100 | (l/h) Flow
| Input Δps: | 10 | (kPa) System pressure drop
Dimension & Type |  |  | Pre-set
DN15/20, High 2,5mm |  |  | 0.8
DN15/20, High 4.0 mm |  |  | 0.5
DN15 Low 5.0 mm |  |  | 1.5
DN15/20, High 5.0 mm |  |  | NOT POSSIBLE
2,5 High | [11 empty] | System DP | Preset
System DP | [10 empty] | Presetting | 5 | 0.6
5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 6 | 0.6
93 | 90 | 86 | 82 | 78 | 73 | 69 | 63 | 58 | 52 | 45 | 0.6 | 7 | 0.7
105.9518 | 101.7952 | 97.4615 | 92.9259 | 88.1572 | 83.1154 | 77.7474 | 71.9801 | 65.7085 | 58.7715 | 50.8976 | 0.7 | 8 | 0.7
118.375 | 113.731 | 108.8891 | 103.8217 | 98.4939 | 92.861 | 86.8635 | 80.42 | 73.413 | 65.6626 | 56.8655 | 0.8 | 9 | 0.8
130.679 | 125.5523 | 120.2072 | 114.6131 | 108.7315 | 102.513 | 95.8922 | 88.7789 | 81.0437 | 72.4877 | 62.7762 | 0.9 | 10 | 0.8
142.8665 | 137.2617 | 131.4181 | 125.3022 | 118.8721 | 112.0737 | 104.8354 | 97.0587 | 88.602 | 79.2481 | 68.6308 | 1 | 11 | 0.9
155.1881 | 149.0999 | 142.7523 | 136.1089 | 129.1243 | 121.7395 | 113.8769 | 105.4295 | 96.2435 | 86.0828 | 74.5499 | 1.1 | 12 | 1
167.4325 | 160.8639 | 154.0155 | 146.848 | 139.3122 | 131.3448 | 122.8618 | 113.748 | 103.8372 | 92.8748 | 80.432 | 1.2 | 13 | 1.1
179.6008 | 172.5549 | 165.2087 | 157.5203 | 149.4369 | 140.8905 | 131.791 | 122.0147 | 111.3837 | 99.6246 | 86.2774 | 1.3 | 14 | 1.3
191.6942 | 184.1738 | 176.333 | 168.1269 | 159.4992 | 150.3773 | 140.6651 | 130.2306 | 118.8837 | 106.3328 | 92.0869 | 1.4 | 15 | 1.5
203.7136 | 195.7217 | 187.3893 | 178.6687 | 169.5 | 159.8061 | 149.4849 | 138.3962 | 126.3378 | 113 | 97.8609 | 1.5
215.6602 | 207.1996 | 198.3785 | 189.1465 | 179.4401 | 169.1778 | 158.2513 | 146.5122 | 133.7468 | 119.6267 | 103.5998 | 1.6 | Sprog | NOT POSSIBLE
227.1845 | 218.2718 | 208.9794 | 199.254 | 189.0289 | 178.2182 | 166.7079 | 154.3415 | 140.8938 | 126.0193 | 109.1359 | 1.7 | Dansk | IKKE MULIGT
238.6078 | 229.2469 | 219.4872 | 209.2728 | 198.5336 | 187.1793 | 175.0902 | 162.102 | 147.9782 | 132.3558 | 114.6235 | 1.8 | Tysk | NICHT MÖGLICH
250.3104 | 240.4904 | 230.252 | 219.5367 | 208.2708 | 196.3596 | 183.6776 | 170.0524 | 155.2359 | 138.8472 | 120.2452 | 1.9 | Engelsk | NOT POSSIBLE
261.9445 | 251.6682 | 240.9539 | 229.7406 | 217.951 | 205.4862 | 192.2147 | 177.9563 | 162.4511 | 145.3007 | 125.8341 | 2
273.5112 | 262.7811 | 251.5937 | 239.8852 | 227.5751 | 214.5598 | 200.7024 | 185.8143 | 169.6245 | 151.7167 | 131.3905 | 2.1
285.0113 | 273.83 | 262.1722 | 249.9714 | 237.1437 | 223.5812 | 209.1411 | 193.627 | 176.7565 | 158.0958 | 136.915 | 2.2
296.0071 | 284.3944 | 272.2869 | 259.6154 | 246.2928 | 232.2071 | 217.2098 | 201.0972 | 183.5758 | 164.1952 | 142.1972 | 2.3
306.9406 | 294.899 | 282.3443 | 269.2047 | 255.39 | 240.784 | 225.2328 | 208.5251 | 190.3565 | 170.26 | 147.4495 | 2.4
318.2486 | 305.7634 | 292.7461 | 279.1225 | 264.7988 | 249.6547 | 233.5306 | 216.2073 | 197.3694 | 176.5326 | 152.8817 | 2.5
329.4934 | 316.567 | 303.0898 | 288.9848 | 274.155 | 258.4759 | 241.782 | 223.8467 | 204.3431 | 182.77 | 158.2835 | 2.6
340.6757 | 327.3106 | 313.3761 | 298.7924 | 283.4593 | 267.248 | 249.9876 | 231.4436 | 211.2781 | 188.9729 | 163.6553 | 2.7
351.7965 | 337.9951 | 323.6057 | 308.5459 | 292.7123 | 275.9718 | 258.148 | 238.9986 | 218.1749 | 195.1416 | 168.9976 | 2.8
362.8564 | 348.6211 | 333.7793 | 318.2461 | 301.9147 | 284.648 | 266.2638 | 246.5124 | 225.034 | 201.2765 | 174.3106 | 2.9
373.8562 | 359.1894 | 343.8977 | 327.8936 | 311.0672 | 293.2769 | 274.3355 | 253.9853 | 231.8558 | 207.3781 | 179.5947 | 3
384.7967 | 369.7007 | 353.9615 | 337.4891 | 320.1702 | 301.8594 | 282.3636 | 261.4179 | 238.6408 | 213.4468 | 184.8504 | 3.1
395.6787 | 380.1558 | 363.9715 | 347.0332 | 329.2246 | 310.3959 | 290.3488 | 268.8107 | 245.3895 | 219.483 | 190.0779 | 3.2
406.5028 | 390.5553 | 373.9282 | 356.5265 | 338.2308 | 318.887 | 298.2915 | 276.1643 | 252.1023 | 225.4872 | 195.2776 | 3.3
417.2698 | 400.8998 | 383.8324 | 365.9698 | 347.1894 | 327.3333 | 306.1923 | 283.479 | 258.7797 | 231.4596 | 200.4499 | 3.4
427.9803 | 411.1902 | 393.6846 | 375.3635 | 356.1011 | 335.7354 | 314.0517 | 290.7554 | 265.4221 | 237.4007 | 205.5951 | 3.5
438.6351 | 421.4269 | 403.4856 | 384.7084 | 364.9664 | 344.0936 | 321.8701 | 297.9938 | 272.0299 | 243.311 | 210.7135 | 3.6
449.2347 | 431.6108 | 413.2359 | 394.0049 | 373.7859 | 352.4087 | 329.6482 | 305.1949 | 278.6036 | 249.1906 | 215.8054 | 3.7
459.78 | 441.7424 | 422.9361 | 403.2538 | 382.5601 | 360.6811 | 337.3863 | 312.359 | 285.1435 | 255.0401 | 220.8712 | 3.8
470.9083 | 452.4341 | 433.1726 | 413.0139 | 391.8194 | 369.4109 | 345.5522 | 319.9192 | 292.0449 | 261.2129 | 226.217 | 3.9
482 | 463 | 443 | 423 | 401 | 378 | 354 | 327 | 299 | 267 | 232 | 4
4,0 High | [11 empty] | System DP | Preset
System DP | [10 empty] | Presetting | 5 | 0.4
5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 6 | 0.4
93 | 89 | 86 | 82 | 77 | 73 | 68 | 63 | 58 | 52 | 45 | 0.4 | 7 | 0.4
120.0273 | 115.3185 | 110.4091 | 105.2709 | 99.8688 | 94.1572 | 88.076 | 81.5425 | 74.4378 | 66.5792 | 57.6593 | 0.5 | 8 | 0.4
146.5298 | 140.7812 | 134.7878 | 128.5151 | 121.9201 | 114.9474 | 107.5234 | 99.5474 | 90.8739 | 81.2801 | 70.3906 | 0.6 | 9 | 0.5
167.8874 | 161.301 | 154.434 | 147.247 | 139.6908 | 131.7017 | 123.1957 | 114.0571 | 104.1194 | 93.1272 | 80.6505 | 0.7 | 10 | 0.5
188.9815 | 181.5676 | 173.8377 | 165.7478 | 157.2422 | 148.2493 | 138.6745 | 128.3877 | 117.2014 | 104.8281 | 90.7838 | 0.8 | 11 | 0.5
209.8194 | 201.588 | 193.0058 | 184.0238 | 174.5803 | 164.5959 | 153.9653 | 142.5442 | 130.1245 | 116.3869 | 100.794 | 0.9 | 12 | 0.6
230.408 | 221.3689 | 211.9445 | 202.0812 | 191.7111 | 180.7469 | 169.0733 | 156.5314 | 142.893 | 127.8074 | 110.6844 | 1 | 13 | 0.6
250.3104 | 240.4904 | 230.252 | 219.5367 | 208.2708 | 196.3596 | 183.6776 | 170.0524 | 155.2359 | 138.8472 | 120.2452 | 1.1 | 14 | 0.7
269.982 | 259.3903 | 248.3474 | 236.7899 | 224.6386 | 211.7913 | 198.1127 | 183.4167 | 167.4358 | 149.7591 | 129.6952 | 1.2 | 15 | 0.8
290.2974 | 278.9087 | 267.0348 | 254.6077 | 241.5421 | 227.728 | 213.0201 | 197.2183 | 180.0348 | 161.028 | 139.4544 | 1.3
310.4385 | 298.2597 | 285.5619 | 272.2726 | 258.3004 | 243.528 | 227.7996 | 210.9014 | 192.5258 | 172.2003 | 149.1298 | 1.4
329.928 | 316.9846 | 303.4897 | 289.366 | 274.5167 | 258.8169 | 242.101 | 224.142 | 204.6127 | 183.0112 | 158.4923 | 1.5
349.2034 | 335.5037 | 321.2204 | 306.2716 | 290.5548 | 273.9377 | 256.2452 | 237.237 | 216.5667 | 193.7032 | 167.7519 | 1.6
368.2699 | 353.8222 | 338.759 | 322.994 | 306.419 | 288.8946 | 270.2362 | 250.1901 | 228.3913 | 204.2794 | 176.9111 | 1.7
387.1327 | 371.9451 | 356.1103 | 339.5379 | 322.1139 | 303.6919 | 284.0778 | 263.0049 | 240.0895 | 214.7426 | 185.9725 | 1.8
406.3618 | 390.4197 | 373.7984 | 356.4028 | 338.1134 | 318.7764 | 298.188 | 276.0684 | 252.0149 | 225.4089 | 195.2099 | 1.9
425.4378 | 408.7474 | 391.3459 | 373.1337 | 353.9857 | 333.7409 | 312.186 | 289.0281 | 263.8453 | 235.9904 | 204.3737 | 2
444.3637 | 426.9309 | 408.7552 | 389.7328 | 369.733 | 348.5876 | 326.0738 | 301.8857 | 275.5827 | 246.4887 | 213.4654 | 2.1
463.1422 | 444.9726 | 426.0289 | 406.2026 | 385.3576 | 363.3186 | 339.8535 | 314.6432 | 287.2286 | 256.9051 | 222.4863 | 2.2
481.3573 | 462.4731 | 442.7843 | 422.1783 | 400.5135 | 377.6077 | 353.2197 | 327.0179 | 298.5251 | 267.009 | 231.2366 | 2.3
499.4335 | 479.8402 | 459.412 | 438.0322 | 415.5538 | 391.7879 | 366.484 | 339.2983 | 309.7355 | 277.0359 | 239.9201 | 2.4
517.7886 | 497.4752 | 476.2962 | 454.1306 | 430.8261 | 406.1868 | 379.9529 | 351.7681 | 321.1188 | 287.2174 | 248.7376 | 2.5
536.0063 | 514.9782 | 493.0541 | 470.1086 | 445.9842 | 420.4779 | 393.3211 | 364.1446 | 332.417 | 297.3228 | 257.4891 | 2.6
554.0891 | 532.3515 | 509.6878 | 485.9683 | 461.03 | 434.6632 | 406.5902 | 376.4294 | 343.6314 | 307.3533 | 266.1758 | 2.7
572.0392 | 549.5975 | 526.1995 | 501.7116 | 475.9654 | 448.7445 | 419.762 | 388.6241 | 354.7637 | 317.3103 | 274.7987 | 2.8
589.859 | 566.7182 | 542.5914 | 517.3406 | 490.7924 | 462.7235 | 432.8382 | 400.7303 | 365.815 | 327.1949 | 283.3591 | 2.9
607.5506 | 583.7158 | 558.8653 | 532.8571 | 505.5127 | 476.6019 | 445.8203 | 412.7494 | 376.7869 | 337.0084 | 291.8579 | 3
625.909 | 601.3539 | 575.7526 | 548.9585 | 520.7878 | 491.0034 | 459.2917 | 425.2214 | 388.1723 | 347.1919 | 300.677 | 3.1
644.1785 | 618.9067 | 592.558 | 564.9819 | 535.9889 | 505.3352 | 472.6978 | 437.6331 | 399.5025 | 357.3259 | 309.4533 | 3.2
662.36 | 636.3749 | 609.2826 | 580.9281 | 551.1168 | 519.5979 | 486.0394 | 449.985 | 410.7782 | 367.4112 | 318.1875 | 3.3
680.4546 | 653.7596 | 625.9272 | 596.7981 | 566.1724 | 533.7925 | 499.3171 | 462.2778 | 422 | 377.4483 | 326.8798 | 3.4
698.061 | 670.6753 | 642.1227 | 612.24 | 580.8219 | 547.6041 | 512.2367 | 474.2391 | 432.9191 | 387.2146 | 335.3377 | 3.5
715.5844 | 687.5112 | 658.2419 | 627.609 | 595.4022 | 561.3506 | 525.0954 | 486.1438 | 443.7866 | 396.9348 | 343.7556 | 3.6
732.5241 | 703.7864 | 673.8242 | 642.4662 | 609.4969 | 574.6392 | 537.5258 | 497.6522 | 454.2922 | 406.3313 | 351.8932 | 3.7
749.3494 | 719.9516 | 689.3012 | 657.2229 | 623.4964 | 587.838 | 549.8721 | 509.0827 | 464.7268 | 415.6643 | 359.9758 | 3.8
767.9236 | 737.7972 | 706.387 | 673.5136 | 638.9511 | 602.4089 | 563.5019 | 521.7014 | 476.246 | 425.9674 | 368.8986 | 3.9
786 | 756 | 723 | 690 | 654 | 617 | 577 | 534 | 488 | 436 | 378 | 4
5,0 Low | [11 empty] | System DP | Preset
System DP | [10 empty] | Presetting | 5 | 1.1
5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 6 | 1.1
59 | 56 | 54 | 51 | 48 | 45 | 42 | 38 | 35 | 32 | 28 | 0.6 | 7 | 1.2
66.8596 | 64.0132 | 61.0342 | 57.9021 | 54.5906 | 51.0649 | 47.2769 | 43.5871 | 40.0228 | 36.1083 | 32.2962 | 0.7 | 8 | 1.3
74.7374 | 71.5556 | 68.2256 | 64.7245 | 61.0228 | 57.0816 | 52.8473 | 48.7228 | 44.7385 | 40.3628 | 36.1016 | 0.8 | 9 | 1.4
82.7018 | 79.181 | 75.4961 | 71.6219 | 67.5258 | 63.1646 | 58.479 | 53.915 | 49.5061 | 44.6641 | 39.9488 | 0.9 | 10 | 1.5
90.6398 | 86.781 | 82.7424 | 78.4964 | 74.0071 | 69.2273 | 64.092 | 59.0899 | 54.2578 | 48.9511 | 43.7832 | 1 | 11 | 1.6
98.387 | 94.1984 | 89.8146 | 85.2056 | 80.3326 | 75.1443 | 69.5701 | 64.1405 | 58.8954 | 53.135 | 47.5254 | 1.1 | 12 | 1.8
106.0838 | 101.5675 | 96.8408 | 91.8713 | 86.6171 | 81.0228 | 75.0126 | 69.1582 | 63.5028 | 57.2918 | 51.2433 | 1.2 | 13 | 2
113.731 | 108.8891 | 103.8217 | 98.4939 | 92.861 | 86.8635 | 80.42 | 74.1435 | 68.0804 | 61.4218 | 54.9373 | 1.3 | 14 | 2.2
121.3292 | 116.1639 | 110.7579 | 105.0742 | 99.0649 | 92.6667 | 85.7927 | 79.097 | 72.6288 | 65.5253 | 58.6076 | 1.4 | 15 | 2.5
129.089 | 123.5933 | 117.8416 | 111.7944 | 105.4007 | 98.5934 | 91.2797 | 84.1557 | 77.2739 | 69.716 | 62.3559 | 1.5
136.8239 | 130.9989 | 124.9026 | 118.493 | 111.7162 | 104.501 | 96.7491 | 89.1983 | 81.9041 | 73.8934 | 66.0922 | 1.6
144.3008 | 138.1575 | 131.728 | 124.9681 | 117.8211 | 110.2115 | 102.036 | 94.0726 | 86.3798 | 77.9313 | 69.7039 | 1.7
151.731 | 145.2714 | 138.5109 | 131.4029 | 123.8879 | 115.8865 | 107.29 | 98.9165 | 90.8276 | 81.9441 | 73.2931 | 1.8
159.3694 | 152.5845 | 145.4837 | 138.0179 | 130.1245 | 121.7204 | 112.6912 | 103.8961 | 95.4 | 86.0693 | 76.9827 | 1.9
166.9837 | 159.8748 | 152.4346 | 144.6122 | 136.3416 | 127.5359 | 118.0753 | 108.8601 | 99.958 | 90.1815 | 80.6608 | 2
174.2979 | 166.8775 | 159.1115 | 150.9464 | 142.3136 | 133.1222 | 123.2472 | 113.6283 | 104.3364 | 94.1316 | 84.1939 | 2.1
181.5676 | 173.8377 | 165.7478 | 157.2422 | 148.2493 | 138.6745 | 128.3877 | 118.3676 | 108.6881 | 98.0577 | 87.7055 | 2.2
188.6555 | 180.6239 | 172.2181 | 163.3805 | 154.0366 | 144.088 | 133.3996 | 122.9884 | 112.931 | 101.8856 | 91.1293 | 2.3
195.7217 | 187.3893 | 178.6687 | 169.5 | 159.8061 | 149.4849 | 138.3962 | 127.595 | 117.1609 | 105.7018 | 94.5426 | 2.4
202.8829 | 194.2456 | 185.2059 | 175.7018 | 165.6532 | 154.9544 | 143.4599 | 132.2635 | 121.4477 | 109.5693 | 98.0018 | 2.5
210.0018 | 201.0614 | 191.7045 | 181.8669 | 171.4657 | 160.3915 | 148.4937 | 136.9044 | 125.7091 | 113.4139 | 101.4405 | 2.6
217.4125 | 208.1566 | 198.4695 | 188.2847 | 177.5165 | 166.0515 | 153.7338 | 141.7356 | 130.1452 | 117.4162 | 105.0202 | 2.7
224.8009 | 215.2305 | 205.2142 | 194.6833 | 183.5492 | 171.6945 | 158.9583 | 146.5523 | 134.568 | 121.4064 | 108.5892 | 2.8
231.8131 | 221.9442 | 211.6154 | 200.756 | 189.2746 | 177.0502 | 163.9166 | 151.1237 | 138.7655 | 125.1934 | 111.9764 | 2.9
238.7848 | 228.619 | 217.9797 | 206.7937 | 194.967 | 182.3749 | 168.8464 | 155.6686 | 142.9389 | 128.9585 | 115.344 | 3
246.0875 | 235.6108 | 224.6461 | 213.118 | 200.9296 | 187.9524 | 174.0101 | 160.4294 | 147.3103 | 132.9024 | 118.8715 | 3.1
253.3686 | 242.582 | 231.2929 | 219.4237 | 206.8746 | 193.5135 | 179.1587 | 165.1761 | 151.6689 | 136.8347 | 122.3887 | 3.2
260.6285 | 249.5328 | 237.9202 | 225.7109 | 212.8023 | 199.0583 | 184.2922 | 169.909 | 156.0147 | 140.7555 | 125.8955 | 3.3
267.8672 | 256.4633 | 244.5281 | 231.9798 | 218.7126 | 204.5869 | 189.4107 | 174.628 | 160.3478 | 144.6648 | 129.3921 | 3.4
274.6751 | 262.9814 | 250.7429 | 237.8756 | 224.2713 | 209.7866 | 194.2246 | 179.0663 | 164.4231 | 148.3415 | 132.6807 | 3.5
281.4451 | 269.4632 | 256.9231 | 243.7386 | 229.799 | 214.9573 | 199.0118 | 183.4798 | 168.4757 | 151.9977 | 135.9509 | 3.6
288.6024 | 276.3157 | 263.4567 | 249.937 | 235.6428 | 220.4237 | 204.0727 | 188.1457 | 172.7601 | 155.8631 | 139.4082 | 3.7
295.7392 | 283.1487 | 269.9717 | 256.1176 | 241.47 | 225.8745 | 209.1192 | 192.7983 | 177.0323 | 159.7174 | 142.8556 | 3.8
302.4125 | 289.5379 | 276.0636 | 261.8969 | 246.9188 | 230.9714 | 213.8379 | 197.1488 | 181.027 | 163.3214 | 146.0791 | 3.9
309 | 296 | 282 | 268 | 252 | 236 | 219 | 201 | 185 | 167 | 149 | 4
5,0 High | [11 empty] | System DP | Preset
System DP | [10 empty] | Presetting | 5 | NOT POSSIBLE
5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 6 | NOT POSSIBLE
198 | 191 | 182 | 174 | 165 | 156 | 146 | 135 | 123 | 110 | 95 | 0.6 | 7 | NOT POSSIBLE
225.8429 | 216.9828 | 207.7452 | 198.0773 | 187.9126 | 177.1657 | 165.7234 | 153.43 | 140.0618 | 125.2751 | 108.4914 | 0.7 | 8 | NOT POSSIBLE
252.9732 | 243.0488 | 232.7015 | 221.8722 | 210.4864 | 198.4485 | 185.6316 | 171.8615 | 156.8873 | 140.3243 | 121.5244 | 0.8 | 9 | NOT POSSIBLE
280.1505 | 269.1599 | 257.701 | 245.7082 | 233.0993 | 219.7681 | 205.5743 | 190.3248 | 173.742 | 155.3995 | 134.5799 | 0.9 | 10 | NOT POSSIBLE
306.9406 | 294.899 | 282.3443 | 269.2047 | 255.39 | 240.784 | 225.2328 | 208.5251 | 190.3565 | 170.26 | 147.4495 | 1 | 11 | NOT POSSIBLE
332.922 | 319.8611 | 306.2437 | 291.9919 | 277.0078 | 261.1655 | 244.298 | 226.176 | 206.4695 | 184.6719 | 159.9306 | 1.1 | 12 | NOT POSSIBLE
358.5469 | 344.4807 | 329.8152 | 314.4664 | 298.3291 | 281.2673 | 263.1015 | 243.5847 | 222.3614 | 198.886 | 172.2404 | 1.2 | 13 | NOT POSSIBLE
383.8265 | 368.7686 | 353.069 | 336.6381 | 319.3629 | 301.0983 | 281.6516 | 260.7588 | 238.0391 | 212.9086 | 184.3843 | 1.3 | 14 | NOT POSSIBLE
408.7714 | 392.7349 | 376.015 | 358.5162 | 340.1184 | 320.6667 | 299.9562 | 277.7055 | 253.5093 | 226.7456 | 196.3674 | 1.4 | 15 | 0.6
433.9867 | 416.9609 | 399.2097 | 380.6315 | 361.0988 | 340.4472 | 318.4592 | 294.8359 | 269.1471 | 240.7325 | 208.4805 | 1.5
458.9395 | 440.9348 | 422.1629 | 402.5165 | 381.8607 | 360.0217 | 336.7695 | 311.788 | 284.6222 | 254.5738 | 220.4674 | 1.6
484.0539 | 465.064 | 445.2649 | 424.5434 | 402.7572 | 379.7232 | 355.1985 | 328.8499 | 300.1975 | 268.5048 | 232.532 | 1.7
508.9137 | 488.9485 | 468.1326 | 446.3469 | 423.4418 | 399.2248 | 373.4406 | 345.7388 | 315.6149 | 282.2945 | 244.4743 | 1.8
533.1112 | 512.1967 | 490.391 | 467.5694 | 443.5753 | 418.2068 | 391.1967 | 362.1777 | 330.6215 | 295.7169 | 256.0983 | 1.9
557.0699 | 535.2155 | 512.4298 | 488.5827 | 463.5102 | 437.0016 | 408.7776 | 378.4545 | 345.4801 | 309.0068 | 267.6077 | 2
581.5454 | 558.7307 | 534.9439 | 510.049 | 483.875 | 456.2017 | 426.7376 | 395.0823 | 360.6591 | 322.5833 | 279.3654 | 2.1
605.8405 | 582.0727 | 557.2922 | 531.3572 | 504.0897 | 475.2604 | 444.5654 | 411.5875 | 375.7263 | 336.0598 | 291.0363 | 2.2
629.5646 | 604.8661 | 579.1152 | 552.1646 | 523.8294 | 493.8711 | 461.9741 | 427.7049 | 390.4394 | 349.2196 | 302.433 | 2.3
653.0651 | 627.4447 | 600.7326 | 572.776 | 543.383 | 512.3064 | 479.2188 | 443.6704 | 405.0138 | 362.2554 | 313.7223 | 2.4
676.7873 | 650.2362 | 622.5538 | 593.5817 | 563.1211 | 530.9156 | 496.6261 | 459.7864 | 419.7257 | 375.4141 | 325.1181 | 2.5
700.3421 | 672.8669 | 644.221 | 614.2407 | 582.7199 | 549.3935 | 513.9106 | 475.7888 | 434.3337 | 388.4799 | 336.4335 | 2.6
724.623 | 696.1953 | 666.5562 | 635.5364 | 602.9228 | 568.441 | 531.7279 | 492.2844 | 449.3921 | 401.9485 | 348.0976 | 2.7
748.789 | 719.4132 | 688.7857 | 656.7314 | 623.0301 | 587.3984 | 549.4609 | 508.7019 | 464.3792 | 415.3534 | 359.7066 | 2.8
772.2981 | 742.0001 | 710.411 | 677.3503 | 642.5909 | 605.8405 | 566.7119 | 524.6733 | 478.959 | 428.3939 | 371 | 2.9
795.6466 | 764.4325 | 731.8884 | 697.8282 | 662.018 | 624.1566 | 583.845 | 540.5354 | 493.4391 | 441.3453 | 382.2163 | 3
819.4252 | 787.2783 | 753.7616 | 718.6834 | 681.803 | 642.81 | 601.2937 | 556.6898 | 508.1859 | 454.5353 | 393.6391 | 3.1
843.0945 | 810.019 | 775.5341 | 739.4428 | 701.497 | 661.3777 | 618.6622 | 572.7699 | 522.865 | 467.6647 | 405.0095 | 3.2
866.6556 | 832.6557 | 797.2072 | 760.1072 | 721.101 | 679.8606 | 635.9513 | 588.7765 | 537.477 | 480.734 | 416.3279 | 3.3
890.1096 | 855.1897 | 818.7818 | 780.6778 | 740.616 | 698.2594 | 653.1619 | 604.7104 | 552.0226 | 493.744 | 427.5948 | 3.4
913.4578 | 877.6219 | 840.259 | 801.1555 | 760.0428 | 716.5753 | 670.2948 | 620.5724 | 566.5025 | 506.6952 | 438.8109 | 3.5
936.7012 | 899.9534 | 861.6397 | 821.5413 | 779.3825 | 734.8088 | 687.3507 | 636.3631 | 580.9174 | 519.5883 | 449.9767 | 3.6
960.2305 | 922.5596 | 883.2836 | 842.1779 | 798.9601 | 753.2668 | 704.6166 | 652.3482 | 595.5097 | 532.64 | 461.2798 | 3.7
983.6554 | 945.0655 | 904.8313 | 862.7228 | 818.4507 | 771.6428 | 721.8057 | 668.2622 | 610.0372 | 545.6338 | 472.5328 | 3.8
1007.756 | 968.2207 | 927.0007 | 883.8605 | 838.5037 | 790.5489 | 739.4908 | 684.6354 | 624.9838 | 559.0025 | 484.1103 | 3.9
1032 | 991 | 949 | 905 | 859 | 809 | 757 | 701 | 640 | 572 | 496 | 4

## ALPHA
Quick - CALC Frese ALPHA
Selection program
|  |  | Input |  | CARTRIDGE SELECTION |  |  |  | Flow | Min. ΔP | Item no. | Item no. | Deviation
| Input Q = |  | 1000 | (l/h) Flow | with selected Valve dimension (DN) |  |  |  | l/h | kPa | LP | HP
| ΔP range (kPa) | DN15-25 | DN25L-50 |  | Nearest higher Flow |  |  |  | 1020 | 12 | 50-33089 | 49-33089 | 2%
| LP Low Press. | 7-350 | 12-350
| HP High Press. | 7-600 | 12-600 |  | Nearest lower Flow |  |  |  | 861 | 12 | 50-33082 | 49-33082 | -13.9%
[7 empty] | Plugs |  | Drain Valve |  | P/T-Plugs
| Dimension Valve house DN | [5 empty] | ALPHA | Item no. | ALPHA | Item no. | ALPHA | Item no.
| Input DN = |  | 50 |  |  |  | 50 | 49-9066 | 50 | 49-9064 | 50 | 49-9061
ALPHA Valve
| Valve | Flow
| Dimension | range
| DN | l/h
| 15 | 25-2448
| 20 | 25-2448
| 25 | 25-2448
| 25L | 674-11355
| 32 | 674-11355
| 40 | 674-11355
| 50 | 674-11355
| Alpha Regler |  | Berechnung nächst kleiner Volumenstrom |  |  |  | Berechnung nächst größer Volumenstrom |  |  |  | Alpha Ventilgehäuse Modell
| Ventil | Vol.- | Vol.- | Min. ΔP | Art.-Nr. | Art.-Nr. | Vol.- | Min. ΔP | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr.
| Dimension | Bereich | Strom |  | LP-Einsatz | HP-Einsatz | Strom |  | LP-Einsatz | HP-Einsatz | Alpha S | Alpha FE | Alpha DM
| DN | L/h | L/h | kPa | bis 3,5 bar | bis 6,0 bar | L/h | kPa | bis 3,5 bar | bis 6,0 bar | IG/IG | IG/IG | IG/IG
| 15 | 25-2448 | 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 49-9006 | 49-9004 | 49-9001
| 20 | 25-2448 | 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 49-9016 | 49-9014 | 49-9011
| 25 | 25-2448 | 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 49-9026 | 49-9024 | 49-9021
| 25L | 674-11355 | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089 | 49-9036 | 49-9034 | 49-9031
| 32 | 674-11355 | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089 | 49-9046 | 49-9044 | 49-9041
| 40 | 674-11355 | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089 | 49-9056 | 49-9054 | 49-9051
| 50 | 674-11355 | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089 | 49-9066 | 49-9064 | 49-9061
| DN15-DN25 | [7 empty] | DN25L-DN50 | [7 empty] | Gehäuse sind mit Stopfen, Druckmessnippel oder Füll- und Entleerungskugelhahn
| Kleiner |  |  |  | Grosser |  |  |  | Kleiner |  |  |  | Grosser
| L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | Der Regelbereich = S ….
|  | DP | LP | HP |  | DP | LP | HP |  | DP | LP | HP |  | DP | LP | HP
| 0 |  |  |  | 25 | 7 | 50-11150 | N/A | 0 |  |  |  | 674 | 12 | 50-33073 | 49-33073
| 25 | 7 | 50-11150 | N/A | 36 | 7 | 50-11170 | N/A | 674 | 12 | 50-33073 | 49-33073 | 861 | 12 | 50-33082 | 49-33082
| 36 | 7 | 50-11170 | N/A | 43 | 7 | 50-11190 | N/A | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089
| 43 | 7 | 50-11190 | N/A | 55 | 7 | 50-11210 | 49-11210 | 1020 | 12 | 50-33089 | 49-33089 | 1136 | 12 | 50-33094 | 49-33094
| 55 | 7 | 50-11210 | 49-11210 | 75 | 8 | 50-11230 | 49-11230 | 1136 | 12 | 50-33094 | 49-33094 | 1190 | 12 | 50-33096 | 49-33096
| 75 | 8 | 50-11230 | 49-11230 | 84 | 9 | 50-11260 | 49-11260 | 1190 | 12 | 50-33096 | 49-33096 | 1272 | 13 | 50-33098 | 49-33098
| 84 | 9 | 50-11260 | 49-11260 | 104 | 10 | 50-11290 | 49-11290 | 1272 | 13 | 50-33098 | 49-33098 | 1349 | 13 | 50-33102 | 49-33102
| 104 | 10 | 50-11290 | 49-11290 | 114 | 10 | 50-11300 | 49-11300 | 1349 | 13 | 50-33102 | 49-33102 | 1485 | 13 | 50-33107 | 49-33107
| 114 | 10 | 50-11300 | 49-11300 | 129 | 11 | 50-11320 | 49-11320 | 1485 | 13 | 50-33107 | 49-33107 | 1567 | 14 | 50-33111 | 49-33111
| 129 | 11 | 50-11320 | 49-11320 | 154 | 11 | 50-11350 | 49-11350 | 1567 | 14 | 50-33111 | 49-33111 | 1631 | 14 | 50-33112 | 49-33112
| 154 | 11 | 50-11350 | 49-11350 | 175 | 12 | 50-11370 | 49-11370 | 1631 | 14 | 50-33112 | 49-33112 | 1815 | 14 | 50-33118 | 49-33118
| 175 | 12 | 50-11370 | 49-11370 | 204 | 12 | 50-11400 | 49-11400 | 1815 | 14 | 50-33118 | 49-33118 | 2001 | 15 | 50-33124 | 49-33124
| 204 | 12 | 50-11400 | 49-11400 | 241 | 12 | 50-11430 | 49-11430 | 2001 | 15 | 50-33124 | 49-33124 | 2044 | 16 | 50-33125 | 49-33125
| 241 | 12 | 50-11430 | 49-11430 | 279 | 12 | 50-11460 | 49-11460 | 2044 | 16 | 50-33125 | 49-33125 | 2171 | 16 | 50-33129 | 49-33129
| 279 | 12 | 50-11460 | 49-11460 | 320 | 13 | 50-11490 | 49-11490 | 2171 | 16 | 50-33129 | 49-33129 | 2271 | 17 | 50-33132 | 49-33132
| 320 | 13 | 50-11490 | 49-11490 | 350 | 13 | 50-11510 | 49-11510 | 2271 | 17 | 50-33132 | 49-33132 | 2380 | 17 | 50-33135 | 49-33135
| 350 | 13 | 50-11510 | 49-11510 | 400 | 13 | 50-11540 | 49-11540 | 2380 | 17 | 50-33135 | 49-33135 | 2498 | 18 | 50-33138 | 49-33138
| 400 | 13 | 50-11540 | 49-11540 | 477 | 14 | 50-11570 | 49-11570 | 2498 | 18 | 50-33138 | 49-33138 | 2639 | 18 | 50-33142 | 49-33142
| 477 | 14 | 50-11570 | 49-11570 | 545 | 14 | 50-11620 | 49-11620 | 2639 | 18 | 50-33142 | 49-33142 | 2871 | 19 | 50-33148 | 49-33148
| 545 | 14 | 50-11620 | 49-11620 | 615 | 14 | 50-11725 | 49-11725 | 2871 | 19 | 50-33148 | 49-33148 | 3191 | 21 | 50-33156 | 49-33156
| 615 | 14 | 50-11725 | 49-11725 | 670 | 14 | 50-11730 | 49-11730 | 3191 | 21 | 50-33156 | 49-33156 | 3407 | 22 | 50-33161 | 49-33161
| 670 | 14 | 50-11730 | 49-11730 | 736 | 14 | 50-11735 | 49-11735 | 3407 | 22 | 50-33161 | 49-33161 | 3486 | 22 | 50-33163 | 49-33163
| 736 | 14 | 50-11735 | 49-11735 | 799 | 16 | 50-11740 | 49-11740 | 3486 | 22 | 50-33163 | 49-33163 | 3634 | 20 | 50-44148 | 49-44148
| 799 | 16 | 50-11740 | 49-11740 | 870 | 19 | 50-11745 | 49-11745 | 3634 | 20 | 50-44148 | 49-44148 | 3681 | 21 | 50-44152 | 49-44152
| 870 | 19 | 50-11745 | 49-11745 | 936 | 21 | 50-11750 | 49-11750 | 3681 | 21 | 50-44152 | 49-44152 | 4088 | 21 | 50-44156 | 49-44156
| 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 4088 | 21 | 50-44156 | 49-44156 | 4315 | 21 | 50-44164 | 49-44164
| 1020 | 22 | 50-20700 | 49-20700 | 1081 | 22 | 50-20740 | 49-20740 | 4315 | 21 | 50-44164 | 49-44164 | 4542 | 22 | 50-44168 | 49-44168
| 1081 | 22 | 50-20740 | 49-20740 | 1195 | 22 | 50-20770 | 49-20770 | 4542 | 22 | 50-44168 | 49-44168 | 4769 | 22 | 50-44173 | 49-44173
| 1195 | 22 | 50-20770 | 49-20770 | 1335 | 23 | 50-20820 | 49-20820 | 4769 | 22 | 50-44173 | 49-44173 | 4996 | 23 | 50-44176 | 49-44176
| 1335 | 23 | 50-20820 | 49-20820 | 1483 | 23 | 50-20860 | 49-20860 | 4996 | 23 | 50-44176 | 49-44176 | 5450 | 24 | 50-44182 | 49-44182
| 1483 | 23 | 50-20860 | 49-20860 | 1581 | 23 | 50-20880 | 49-20880 | 5450 | 24 | 50-44182 | 49-44182 | 5905 | 25 | 50-44191 | 49-44191
| 1581 | 23 | 50-20880 | 49-20880 | 1774 | 24 | 50-20920 | 49-20920 | 5905 | 25 | 50-44191 | 49-44191 | 6539 | 26 | 50-44194 | 49-44194
| 1774 | 24 | 50-20920 | 49-20920 | 1883 | 24 | 50-20940 | 49-20940 | 6539 | 26 | 50-44194 | 49-44194 | 6831 | 27 | 50-44200 | 49-44200
| 1883 | 24 | 50-20940 | 49-20940 | 2080 | 25 | 50-20990 | 49-20990 | 6831 | 27 | 50-44200 | 49-44200 | 7267 | 28 | 50-44205 | 49-44205
| 2080 | 25 | 50-20990 | 49-20990 | 2251 | 26 | 50-21030 | 49-21030 | 7267 | 28 | 50-44205 | 49-44205 | 7721 | 30 | 50-44211 | 49-44211
| 2251 | 26 | 50-21030 | 49-21030 | 2319 | 27 | 50-21060 | 49-21060 | 7721 | 30 | 50-44211 | 49-44211 | 8176 | 31 | 50-44217 | 49-44217
| 2319 | 27 | 50-21060 | 49-21060 | 2448 | 28 | 50-21090 | 49-21090 | 8176 | 31 | 50-44217 | 49-44217 | 8630 | 33 | 50-44222 | 49-44222
| 2448 | 28 | 50-21090 | 49-21090 | 2448 | 28 | 50-21090 | 49-21090 | 8630 | 33 | 50-44222 | 49-44222 | 9084 | 34 | 50-44229 | 49-44229
[9 empty] | 9084 | 34 | 50-44229 | 49-44229 | 9538 | 36 | 50-44235 | 49-44235
[9 empty] | 9538 | 36 | 50-44235 | 49-44235 | 9990 | 38 | 50-44241 | 49-44241
[9 empty] | 9990 | 38 | 50-44241 | 49-44241 | 10445 | 40 | 50-44248 | 49-44248
[9 empty] | 10445 | 40 | 50-44248 | 49-44248 | 10900 | 42 | 50-44250 | 49-44250
[9 empty] | 10900 | 42 | 50-44250 | 49-44250 | 11355 | 44 | 50-44262 | 49-44262
[9 empty] | 11355 | 44 | 50-44262 | 49-44262 | 11355 | 44 | 50-44262 | 49-44262

## ALPHA Wafer
QUICK - CALC Frese ALPHA Wafer
Selection program
|  |  | Input |  | CARTRIDGE SELECTION |  |  | Flow | Min. ΔP | Qty | Vare nr. | Flow |  | Qty | Item no. | Flow | Deviation
| Input Q = |  | 5000 | m³/h Flow | with selected Valve dimension |  |  | m³/h | kPa | Cartriges |  |  |  | Cartridges
[5 empty] | Nearest higher Flow |  |  | 675 | 49 | 13 | 52-66407H | 45 |  | 2 | 52-66407H | 45 | -86.5%
Cartridge Type HP (High Pressure)
| AISI 304 |  |  |  | Nearest lower Flow |  |  | 675 | 49 | 15 | 52-66407H | 45 |  |  |  |  | -86.5%
ΔP range: 13 - 600 kPa
Dimension Valve house DN
| Input DN = |  | 300
| Item no. Valve house |  | 49-9143-01
|  |  | Berechnungen Nächst kleiner Volumenstrom : |  |  |  |  | Berechnungen Nächst größer Volumenstrom :
Ventil | Vol.-Ber. | Anzahl | Vol.-Str | Min ΔP | Art.-Nr. | Vol.-Strom | Ist/Soll | Vol.-Strom | Min. ΔP | Anzahl | Art.-Nr. | Vol.- | Anz | Rest | Art.-Nr. | Vol.- | Ist/Soll
Dim. | m³/h | Einsätze | m³/h | kPa |  | m³/h | Abw. | m³/h | kPa | Einsätze |  | Strom | Eins | Vol.-Str |  | Strom | Abw.
DN |  |  | Regler Komplett |  | Einsatz | Einsatz |  | Regler Komplett |  |  | Einsatz | Eins. |  | m³/h | Einsatz | Eins.
50 | 3,8 - 45 | 1 | 45 | 49 | 52-66407H | 45 | -99.1% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 4955 | 0 | 0 | -99.1%
65 | 3,8 - 45 | 1 | 45 | 49 | 52-66407H | 45 | -99.1% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 4955 | 0 | 0 | -99.1%
80 | 3,8 - 45 | 1 | 45 | 49 | 52-66407H | 45 | -99.1% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 4955 | 0 | 0 | -99.1%
100 | 3,8 - 90 | 2 | 90 | 49 | 52-66407H | 45 | -98.2% | 90 | 49 | 1 | 52-66407H | 45 | 1 | 4955 | 52-66407H | 45 | -98.2%
125 | 3,8 - 135 | 3 | 135 | 49 | 52-66407H | 45 | -97.3% | 135 | 49 | 2 | 52-66407H | 45 | 1 | 4910 | 52-66407H | 45 | -97.3%
150 | 3,8 - 180 | 4 | 180 | 49 | 52-66407H | 45 | -96.4% | 180 | 49 | 3 | 52-66407H | 45 | 1 | 4865 | 52-66407H | 45 | -96.4%
200 | 3,8 - 315 | 7 | 315 | 49 | 52-66407H | 45 | -93.7% | 315 | 49 | 6 | 52-66407H | 45 | 1 | 4730 | 52-66407H | 45 | -93.7%
250 | 3,8 - 540 | 12 | 540 | 49 | 52-66407H | 45 | -89.2% | 540 | 49 | 10 | 52-66407H | 45 | 2 | 2275 | 52-66407H | 45 | -89.2%
300 | 3,8 - 675 | 15 | 675 | 49 | 52-66407H | 45 | -86.5% | 675 | 49 | 13 | 52-66407H | 45 | 2 | 2207.5 | 52-66407H | 45 | -86.5%
350 | 3,8 - 855 | 19 | 855 | 49 | 52-66407H | 45 | -82.9% | 855 | 49 | 16 | 52-66407H | 45 | 3 | 1426.6667 | 52-66407H | 45 | -82.9%
400 | 3,8 - 1170 | 26 | 1170 | 49 | 52-66407H | 45 | -76.6% | 1170 | 49 | 21 | 52-66407H | 45 | 5 | 811 | 52-66407H | 45 | -76.6%
450 | 3,8 - 1485 | 33 | 1485 | 49 | 52-66407H | 45 | -70.3% | 1485 | 49 | 23 | 52-66407H | 45 | 10 | 396.5 | 52-66407H | 45 | -70.3%
500 | 3,8 - 1800 | 40 | 1800 | 49 | 52-66407H | 45 | -64% | 1800 | 49 | 30 | 52-66407H | 45 | 10 | 365 | 52-66407H | 45 | -64%
600 | 3,8 - 2520 | 56 | 2520 | 49 | 52-66407H | 45 | -49.6% | 2520 | 49 | 41 | 52-66407H | 45 | 15 | 210.3333 | 52-66407H | 45 | -49.6%
800 | 3,8 - 3825 | 85 | 3825 | 49 | 52-66407H | 45 | -23.5% | 3825 | 49 | 65 | 52-66407H | 45 | 20 | 103.75 | 52-66407H | 45 | -23.5%
900 | 3,8 - 5040 | 112 | 4592 | 46 | 52-66407 | 41 | -8.16% | 5040 | 49 | 92 | 52-66407H | 45 | 20 | 43 | 52-66407H | 45 | 0.8%
1000 | 3,8 - 6120 | 136 | 4936.8 | 42 | 52-66393 | 36.3 | -1.264% | 5019.2 | 43 | 116 | 52-66398 | 37.7 | 20 | 31.34 | 52-66379 | 32.3 | 0.384%
| '=((SVERWEIS(($D$5/$C17);$D$40:$F$84;1)*C17)) | [6 empty] | Flow > | =((SVERWEIS(($D$5/$C22);$C$38:$I$81;1)*(C22-1)))
| '=WENN($D$5/$C23<3,8;SVERWEIS(($D$5/$C22);$D$40:$F$84;1);SVERWEIS(($D$5/$C23);$D$40:$F$84;1)) | [10 empty] | Korrektion til slut :
| '=WENN($D$5/$C24<3,8;D23;SVERWEIS(($D$5/$C24);$D$40:$F$84;1)) | [10 empty] | Spalte D:H Min el slettes
DN50-DN800
|  | Kleiner |  |  |  | Grosser | [5 empty] | WENN(Prüfung;Dann_Wert; WENN(Prüfung;Dann_Wert;Sonst_Wert))
|  | L/h | m³/h | Min |  | m³/h | Min
|  |  |  | DP | Vare nr. |  | DP | Vare nr. |  |  |  | SVERWEIS(Suchkriterium;Matrix;Spalteindex;Bereich_Verweis)
0
|  |  | 0 |  |  | 3.8 | 13 | 52-55179 |  | 45 | D | '=((SVERWEIS(($D$5/$C17);$D$40:$F$84;1)*C17))
|  | 3820 | 3.8 | 13 | 52-55179 | 3.9 | 13 | 52-55184 |  | 49 | E | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;2)
|  | 3931 | 3.9 | 13 | 52-55184 | 4 | 13 | 52-55189 |  | 52-66407H | F | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;3)
|  | 4049 | 4 | 13 | 52-55189 | 4.2 | 13 | 52-55194 |  | 45 | G | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;1)
|  | 4199 | 4.2 | 13 | 52-55194 | 4.4 | 13 | 52-55200
|  | 4399 | 4.4 | 13 | 52-55200 | 4.6 | 14 | 52-55206
|  | 4640 | 4.6 | 14 | 52-55206 | 5 | 14 | 52-55213 |  | WENN(O23<0;
|  | 4951 | 5 | 14 | 52-55213 | 5.3 | 14 | 52-55220
|  | 5310 | 5.3 | 14 | 52-55220 | 5.7 | 14 | 52-55227
|  | 5700 | 5.7 | 14 | 52-55227 | 6.2 | 14 | 52-55235 |  | DN | Art.-Nr. Gehäuse
|  | 6209 | 6.2 | 14 | 52-55235 | 6.5 | 14 | 52-55243 |  | 50 | 49-9073-01
|  | 6511 | 6.5 | 14 | 52-55243 | 7.1 | 14 | 52-55251 |  | 65 | 49-9083-01
|  | 7081 | 7.1 | 14 | 52-55251 | 7.9 | 15 | 52-55260 |  | 80 | 49-9093-01
|  | 7901 | 7.9 | 15 | 52-55260 | 8.9 | 16 | 52-55269 |  | 100 | 49-9103-01
|  | 8900 | 8.9 | 16 | 52-55269 | 10.4 | 19 | 52-55279 |  | 125 | 49-9163-01
|  | 10399 | 10.4 | 19 | 52-55279 | 11.4 | 22 | 52-55287 |  | 150 | 49-9113-01
|  | 11355 | 11.4 | 22 | 52-55287 | 12.5 | 23 | 52-55292 |  | 200 | 49-9123-01
|  | 12491 | 12.5 | 23 | 52-55292 | 13.4 | 24 | 52-55298 |  | 250 | 49-9133-01
|  | 13399 | 13.4 | 24 | 52-55298 | 14.8 | 27 | 52-55303 |  | 300 | 49-9143-01
|  | 14762 | 14.8 | 27 | 52-55303 | 16 | 29 | 52-55308 |  | 350 | 49-9153-01
|  | 15999 | 16 | 29 | 52-55308 | 17 | 34 | 52-66285 |  | 400 | 49-9173-01
|  | 17037 | 17 | 34 | 52-66285 | 18.1 | 34 | 52-66292 |  | 450 | 49-9183-01
|  | 18148 | 18.1 | 34 | 52-66292 | 18.8 | 35 | 52-66301 |  | 500 | 49-9193-01
|  | 18797 | 18.8 | 35 | 52-66301 | 19.5 | 35 | 52-66305 |  | 600 | 49-9203-01
|  | 19467 | 19.5 | 35 | 52-66305 | 20.5 | 35 | 52-66312 |  | 800 | 49-9213-01
|  | 20464 | 20.5 | 35 | 52-66312 | 21.5 | 36 | 52-66319 |  | 900 | 49-9233-01
|  | 21527 | 21.5 | 36 | 52-66319 | 22.4 | 36 | 52-66326 |  | 1000 | 49-9223-01
|  | 22449 | 22.4 | 36 | 52-66326 | 23.5 | 36 | 52-66332
|  | 23482 | 23.5 | 36 | 52-66332 | 24.5 | 37 | 52-66338
|  | 24531 | 24.5 | 37 | 52-66338 | 25.6 | 38 | 52-66344
|  | 25621 | 25.6 | 38 | 52-66344 | 26.5 | 38 | 52-66349
|  | 26528 | 26.5 | 38 | 52-66349 | 27.7 | 38 | 52-66356
|  | 27686 | 27.7 | 38 | 52-66356 | 29.2 | 38 | 52-66362
|  | 29157 | 29.2 | 38 | 52-66362 | 30 | 39 | 52-66367
|  | 29954 | 30 | 39 | 52-66367 | 31 | 39 | 52-66373
|  | 30976 | 31 | 39 | 52-66373 | 32.3 | 40 | 52-66379
|  | 32260 | 32.3 | 40 | 52-66379 | 33.6 | 40 | 52-66385
|  | 33565 | 33.6 | 40 | 52-66385 | 35 | 40 | 52-66391
|  | 34953 | 35 | 40 | 52-66391 | 36.3 | 42 | 52-66393
|  | 36336 | 36.3 | 42 | 52-66393 | 37.7 | 43 | 52-66398
|  | 37685 | 37.7 | 43 | 52-66398 | 38.6 | 44 | 52-66400
|  | 38607 | 38.6 | 44 | 52-66400 | 41 | 46 | 52-66407
|  | 40971 | 41 | 46 | 52-66407 | 45 | 49 | 52-66407H
|  | 45000 | 45 | 49 | 52-66407H | 45 | 49 | 52-66407H
Valve | Flow | Qty
Dim. | m³/h | Cartridges
DN
50 | 3,8 - 45 | 1
65 | 3,8 - 45 | 1
80 | 3,8 - 45 | 1
100 | 3,8 - 90 | 2
125 | 3,8 - 135 | 3
150 | 3,8 - 180 | 4
200 | 3,8 - 315 | 7
250 | 3,8 - 540 | 12
300 | 3,8 - 675 | 15
350 | 3,8 - 855 | 19
400 | 3,8 - 1170 | 26
450 | 3,8 - 1485 | 33
500 | 3,8 - 1800 | 40
600 | 3,8 - 2520 | 56
800 | 3,8 - 3825 | 85
900 | 3,8 - 5040 | 112
1000 | 3,8 - 6120 | 136

## Frese EVA
Quick - CALC Frese EVA
Selection program
|  | Input |  | CARTRIDGE SELECTION |  |  |  | Flow | Min. ΔP kPa | Min. ΔP kPa | Item no. | Item no. | Deviation
| Input Q = | 1500 | (l/h) Flow | with selected Valve dimension (DN) |  |  |  | l/h | Cartridge | total valve | LP | HP
| ΔP range (kPa) | DN15-25 |  | Nearest higher Flow |  |  |  | 1581 | 23 | 51 | 50-20880 | 49-20880 | 5.4%
| LP Low Press. | 7-350
| HP High Press. | 7-600 |  | Nearest lower Flow |  |  |  | 1483 | 23 | 47 | 50-20860 | 49-20860 | -1.133%
Dimension Valve house DN ; Kvs = 3,0
| Input DN = | 15
Frese EVA with Plugs
| EVA F/F | Item no.
| 15 | 48-5803
Frese EVA with P/T plugs
| EVA F/F | Item no.
| 15 | 48-5800
|  |  |  | Actuator (NC) |  | Item no.
| Male/Male |  |  | 24 V On/Off |  | 48-5525
| EVA Basic | Item no. |  | 230 V On/Off |  | 48-5526
| 15 | 48-5806
| EVA | Berechnung nächst kleiner Volumenstrom |  |  |  |  | Berechnung nächst größer Volumenstrom |  |  |  |  | EVA Ventilgehäuse
| Ventil | Vol.- | Min. ΔP | Min. ΔP | Art.-Nr. | Art.-Nr. | Vol.- | Min. ΔP | Min. ΔP | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr.
| Dimension | Strom | Einsatz | Ges. Ventil | LP-Einsatz | HP-Einsatz | Strom | Einsatz | Ges. Ventil | LP-Einsatz | HP-Einsatz | EVA S | EVA DM
| DN | L/h | kPa | kPa | bis 3,5 bar | bis 6,0 bar | L/h | kPa | kPa | bis 3,5 bar | bis 6,0 bar | IG/IG | IG/IG
| 15 | 1483 | 23 | 47 | 50-20860 | 49-20860 | 1581 | 23 | 51 | 50-20880 | 49-20880 | 48-5803 | 48-5800
| 20 | 1483 | 23 | 47 | 50-20860 | 49-20860 | 1581 | 23 | 51 | 50-20880 | 49-20880 | 48-5804 | 48-5801
| 25 | 1483 | 23 | 47 | 50-20860 | 49-20860 | 1581 | 23 | 51 | 50-20880 | 49-20880 | 48-5805 | 48-5802
| EVA Basic | [10 empty] | EVA Basic
| 15 | 1483 | 23 | 47 | 50-20860 | 49-20860 | 1581 | 23 | 51 | 50-20880 | 49-20880 | 48-5806
| DN15-DN25 | [14 empty] | Gehäuse sind mit Stopfen, Druckmessnippel oder Füll- und Entleerungskugelhahn
| Kleiner |  |  |  |  | Grosser
| L/h | Min | Min DP To |  |  | L/h | Min | Min DP To | Vare nr. | [6 empty] | Der Regelbereich = S ….
|  | DP | Geh.+Eins. | LP | HP |  | DP | Geh+Ein | LP | HP
| 0 |  |  |  |  | 25 | 7 | 7 | 50-11150 | N/A
| 25 | 7 | 7 | 50-11150 | N/A | 36 | 7 | 7 | 50-11170 | N/A
| 36 | 7 | 7 | 50-11170 | N/A | 43 | 7 | 7 | 50-11190 | N/A
| 43 | 7 | 7 | 50-11190 | N/A | 55 | 7 | 7 | 50-11210 | 49-11210
| 55 | 7 | 7 | 50-11210 | 49-11210 | 75 | 8 | 8 | 50-11230 | 49-11230
| 75 | 8 | 8 | 50-11230 | 49-11230 | 84 | 9 | 9 | 50-11260 | 49-11260
| 84 | 9 | 9 | 50-11260 | 49-11260 | 104 | 10 | 10 | 50-11290 | 49-11290
| 104 | 10 | 10 | 50-11290 | 49-11290 | 114 | 10 | 10 | 50-11300 | 49-11300
| 114 | 10 | 10 | 50-11300 | 49-11300 | 129 | 11 | 11 | 50-11320 | 49-11320
| 129 | 11 | 11 | 50-11320 | 49-11320 | 154 | 11 | 11 | 50-11350 | 49-11350 |  |  |  | 50-33112 | 49-33112
| 154 | 11 | 11 | 50-11350 | 49-11350 | 175 | 12 | 12 | 50-11370 | 49-11370 |  |  |  | 50-33118 | 49-33118
| 175 | 12 | 12 | 50-11370 | 49-11370 | 204 | 12 | 12 | 50-11400 | 49-11400 |  |  |  | 50-33124 | 49-33124
| 204 | 12 | 12 | 50-11400 | 49-11400 | 241 | 12 | 13 | 50-11430 | 49-11430 |  |  |  | 50-33125 | 49-33125
| 241 | 12 | 13 | 50-11430 | 49-11430 | 279 | 12 | 13 | 50-11460 | 49-11460 |  |  |  | 50-33129 | 49-33129
| 279 | 12 | 13 | 50-11460 | 49-11460 | 320 | 13 | 14 | 50-11490 | 49-11490 |  |  |  | 50-33132 | 49-33132
| 320 | 13 | 14 | 50-11490 | 49-11490 | 350 | 13 | 14 | 50-11510 | 49-11510 |  |  |  | 50-33135 | 49-33135
| 350 | 13 | 14 | 50-11510 | 49-11510 | 400 | 13 | 15 | 50-11540 | 49-11540 |  |  |  | 50-33138 | 49-33138
| 400 | 13 | 15 | 50-11540 | 49-11540 | 477 | 14 | 17 | 50-11570 | 49-11570 |  |  |  | 50-33142 | 49-33142
| 477 | 14 | 17 | 50-11570 | 49-11570 | 545 | 14 | 17 | 50-11620 | 49-11620 |  |  |  | 50-33148 | 49-33148
| 545 | 14 | 17 | 50-11620 | 49-11620 | 615 | 14 | 18 | 50-11725 | 49-11725 |  |  |  | 50-33156 | 49-33156
| 615 | 14 | 18 | 50-11725 | 49-11725 | 670 | 14 | 19 | 50-11730 | 49-11730 |  |  |  | 50-33161 | 49-33161
| 670 | 14 | 19 | 50-11730 | 49-11730 | 736 | 14 | 20 | 50-11735 | 49-11735 |  |  |  | 50-33163 | 49-33163
| 736 | 14 | 20 | 50-11735 | 49-11735 | 799 | 16 | 23 | 50-11740 | 49-11740 |  |  |  | 50-44148 | 49-44148
| 799 | 16 | 23 | 50-11740 | 49-11740 | 870 | 19 | 27 | 50-11745 | 49-11745 |  |  |  | 50-44152 | 49-44152
| 870 | 19 | 27 | 50-11745 | 49-11745 | 936 | 21 | 31 | 50-11750 | 49-11750 |  |  |  | 50-44156 | 49-44156
| 936 | 21 | 31 | 50-11750 | 49-11750 | 1020 | 22 | 34 | 50-20700 | 49-20700 |  |  |  | 50-44164 | 49-44164
| 1020 | 22 | 34 | 50-20700 | 49-20700 | 1081 | 22 | 35 | 50-20740 | 49-20740 |  |  |  | 50-44168 | 49-44168
| 1081 | 22 | 35 | 50-20740 | 49-20740 | 1195 | 22 | 38 | 50-20770 | 49-20770 |  |  |  | 50-44173 | 49-44173
| 1195 | 22 | 38 | 50-20770 | 49-20770 | 1335 | 23 | 43 | 50-20820 | 49-20820 |  |  |  | 50-44176 | 49-44176
| 1335 | 23 | 43 | 50-20820 | 49-20820 | 1483 | 23 | 47 | 50-20860 | 49-20860 |  |  |  | 50-44182 | 49-44182
| 1483 | 23 | 47 | 50-20860 | 49-20860 | 1581 | 23 | 51 | 50-20880 | 49-20880 |  |  |  | 50-44191 | 49-44191
| 1581 | 23 | 51 | 50-20880 | 49-20880 | 1774 | 24 | 59 | 50-20920 | 49-20920 |  |  |  | 50-44194 | 49-44194
| 1774 | 24 | 59 | 50-20920 | 49-20920 | 1883 | 24 | 61 | 50-20940 | 49-20940 |  |  |  | 50-44200 | 49-44200
| 1883 | 24 | 61 | 50-20940 | 49-20940 | 2080 | 25 | 73 | 50-20990 | 49-20990 |  |  |  | 50-44205 | 49-44205
| 2080 | 25 | 73 | 50-20990 | 49-20990 | 2251 | 26 | 82 | 50-21030 | 49-21030 |  |  |  | 50-44211 | 49-44211
| 2251 | 26 | 82 | 50-21030 | 49-21030 | 2319 | 27 | 87 | 50-21060 | 49-21060 |  |  |  | 50-44217 | 49-44217
| 2319 | 27 | 87 | 50-21060 | 49-21060 | 2448 | 28 | 95 | 50-21090 | 49-21090 |  |  |  | 50-44222 | 49-44222
| 2448 | 28 | 95 | 50-21090 | 49-21090 | 2448 | 28 | 95 | 50-21090 | 49-21090 |  |  |  | 50-44229 | 49-44229
[14 empty] | 50-44235 | 49-44235
[14 empty] | 50-44241 | 49-44241
[14 empty] | 50-44248 | 49-44248
[14 empty] | 50-44250 | 49-44250
[14 empty] | 50-44262 | 49-44262
[14 empty] | 50-44262 | 49-44262
EVA
| Valve | Flow
Dimension
| DN | l/h
| 15 | 25-2448
| 20 | 25-2448
| 25 | 25-2448
EVA Basic
| 15 | 25-2448

## COMBIFLOW
QUICK - CALC COMBIFLOW 6-Way
Setting & Selection program
Input
Input dP = | 400 | (kPa) Differential pressure across valve
Flow cooling | 800 | l/h
Flow heating | 500 | l/h
|  |  | Calculation Pre-set |  | Calculation minimum diff. Pressure |  | Calculation total pressure loss
Dimension | Range |  | Cooling | Heating | Cooling | Heating | Cooling | Heating
| Flow l/h | Range ∆Pp (kPa) | Pre-set scale | Pre-set scale | Min. ∆P (kPa) | Min. ∆P (kPa) | Total ∆P (kPa) | Total ∆P (kPa)
DN15 Low | 30 - 830 | 4 - 400 | 3.8 | 3 | 18 | 15 | 25 | 18
DN15 | 210 - 1200 | 15 - 400 | 2.8 | 2 | 18 | 15 | 25 | 17
DN20 | 460 - 4250 | 17-400 | 1.4 | 1 | 17 | 17 | 18 | 17
Bacnet Value = 1 x Preset Scale
Modbus Value = 10 x Preset scale
Analog Pre-set
Dimension | Cooling |  | Heating
| Voltage preset 0-10V | Current preset 4-20mA | Voltage preset 0-10V | Current preset 4-20mA
DN15 Low | 0.2 | 4.3 | 8.9 | 18.2
DN15 | 1.3 | 6.1 | 7.8 | 16.5
DN20 | 2.9 | 8.6 | 6.7 | 14.7
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
|  |  | Køling | Varme | Vinkel køling | Vinkel varme |  | Best Match
Type | Min | Max | Evaluering Flow | Evaluering Flow | -43 | -35 |  |  | DN15 Low | DN15 | DN20
DN15 Low | 30 | 830 | 800 | 500 | -33 | -25 |  | Cooling | 780 | 810 | 740
DN15 | 210 | 1200 | 800 | 800 | -19 | -15 |  | Heating | 460 | 490 | 460
DN20 | 460 | 4250 | 800 | 800
Flow |  |  | Preset | Minimum DP |  |  | Total pumpe DP
DN15 Low | DN15 | DN20 |  | DN15 Low | DN15 | DN20 | DN15 Low | DN15 | DN20
30 |  |  | 0.5 | 4 |  |  | 10
35 |  |  | 0.6 | 4 |  |  | 10
50 |  |  | 0.8 | 5 |  |  | 10
65 | 210 | 460 | 1 | 8 | 15 | 17 | 10 | 15 | 17
75 | 260 | 600 | 1.2 | 10 | 15 | 17 | 11 | 15 | 18
85 | 320 | 740 | 1.4 | 11 | 15 | 17 | 12 | 16 | 18
100 | 380 | 910 | 1.6 | 11 | 15 | 18 | 12 | 16 | 19
120 | 430 | 1110 | 1.8 | 12 | 15 | 18 | 13 | 17 | 19
140 | 490 | 1310 | 2 | 13 | 15 | 18 | 14 | 17 | 20
190 | 550 | 1540 | 2.2 | 14 | 16 | 19 | 15 | 19 | 22
240 | 610 | 1760 | 2.4 | 14 | 17 | 20 | 15 | 21 | 24
310 | 700 | 2020 | 2.6 | 14 | 17 | 21 | 15 | 23 | 26
380 | 810 | 2310 | 2.8 | 14 | 18 | 22 | 16 | 25 | 28
460 | 910 | 2600 | 3 | 15 | 19 | 23 | 18 | 27 | 30
560 | 1000 | 3000 | 3.2 | 15 | 20 | 26 | 19 | 29 | 35
660 | 1090 | 3400 | 3.4 | 16 | 21 | 29 | 21 | 31 | 40
730 | 1150 | 3730 | 3.6 | 17 | 21 | 32 | 23 | 32 | 46
780 | 1170 | 3990 | 3.8 | 18 | 22 | 35 | 25 | 34 | 51
830 | 1200 | 4250 | 4 | 19 | 23 | 38 | 26 | 36 | 56
|  |  | DN15 LOW |  |  |  | DN15 |  |  |  | DN20
Flow |  |  | Voltage |  | Current |  | Voltage |  | Current |  | Voltage |  | Current
DN15 Low | DN15 | DN20 | Heating | Cooling | Heating | Cooling | Heating | Cooling | Heating | Cooling | Heating | Cooling | Heating | Cooling
30 |  |  | 6.1 | 3.9 | 13.8 | 10.2
35 |  |  | 6.2 | 3.8 | 13.9 | 10.1
50 |  |  | 6.5 | 3.5 | 14.4 | 9.6
65 | 210 | 460 | 6.7 | 3.3 | 14.7 | 9.3 | 6.7 | 3.3 | 14.7 | 9.3 | 6.7 | 3.3 | 14.7 | 9.3
75 | 260 | 600 | 6.9 | 3.1 | 15 | 9 | 6.9 | 3.1 | 15 | 9 | 6.9 | 3.1 | 15 | 9
85 | 320 | 740 | 7.1 | 2.9 | 15.4 | 8.6 | 7.1 | 2.9 | 15.4 | 8.6 | 7.1 | 2.9 | 15.4 | 8.6
100 | 380 | 910 | 7.3 | 2.7 | 15.7 | 8.3 | 7.3 | 2.7 | 15.7 | 8.3 | 7.3 | 2.7 | 15.7 | 8.3
120 | 430 | 1110 | 7.6 | 2.4 | 16.2 | 7.8 | 7.6 | 2.4 | 16.2 | 7.8 | 7.6 | 2.4 | 16.2 | 7.8
140 | 490 | 1310 | 7.8 | 2.2 | 16.5 | 7.5 | 7.8 | 2.2 | 16.5 | 7.5 | 7.8 | 2.2 | 16.5 | 7.5
190 | 550 | 1540 | 8 | 2 | 16.8 | 7.2 | 8 | 2 | 16.8 | 7.2 | 8 | 2 | 16.8 | 7.2
240 | 610 | 1760 | 8.2 | 1.8 | 17.1 | 6.9 | 8.2 | 1.8 | 17.1 | 6.9 | 8.2 | 1.8 | 17.1 | 6.9
310 | 700 | 2020 | 8.4 | 1.6 | 17.4 | 6.6 | 8.4 | 1.6 | 17.4 | 6.6 | 8.4 | 1.6 | 17.4 | 6.6
380 | 810 | 2310 | 8.7 | 1.3 | 17.9 | 6.1 | 8.7 | 1.3 | 17.9 | 6.1 | 8.7 | 1.3 | 17.9 | 6.1
460 | 910 | 2600 | 8.9 | 1.1 | 18.2 | 5.8 | 8.9 | 1.1 | 18.2 | 5.8 | 8.9 | 1.1 | 18.2 | 5.8
560 | 1000 | 3000 | 9.1 | 0.9 | 18.6 | 5.4 | 9.1 | 0.9 | 18.6 | 5.4 | 9.1 | 0.9 | 18.6 | 5.4
660 | 1090 | 3400 | 9.3 | 0.7 | 18.9 | 5.1 | 9.3 | 0.7 | 18.9 | 5.1 | 9.3 | 0.7 | 18.9 | 5.1
730 | 1150 | 3730 | 9.5 | 0.5 | 19.2 | 4.8 | 9.5 | 0.5 | 19.2 | 4.8 | 9.5 | 0.5 | 19.2 | 4.8
780 | 1170 | 3990 | 9.8 | 0.2 | 19.7 | 4.3 | 9.8 | 0.2 | 19.7 | 4.3 | 9.8 | 0.2 | 19.7 | 4.3
830 | 1200 | 4250 | 10 | 0 | 20 | 4 | 10 | 0 | 20 | 4 | 10 | 0 | 20 | 4

## OPTIMIZER 6 way
QUICK - CALC OPTIMIZER 6-Way
Setting & Selection program
Input
Input dP = | 400 | (kPa) Differential pressure across valve
Flow cooling | 1800 | l/h
Flow heating | 200 | l/h
OPTIMA Compact
Dimension | Range |  | Calculation cooling |  | Total OPTIMIZER | Calculation heating
| Flow l/h | Range ∆Pp (kPa) | Pre-set | Min. ∆P (kPa) | Min. ∆P (kPa) | Pre-set
DN15 Low 5,0 | 65-370 | 14-600 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
DN15 High 5,0 | 220-1330 | 16-600 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
DN20 High 5,5 | 300-1800 | 18-600 | 4 | 40 | 57.9377 | 11.11%
DN25L 5,5 | 600-3609 | 17-800 | 1.956 | 17.9348 | 35.8725 | 11.11%
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 Low 5,0 | 0.9 | 65 | 370 | UDEN FOR OMRÅDET | 600
DN15 High 5,0 | 2.7 | 220 | 1330 | UDEN FOR OMRÅDET | 600
DN 20 High 5,5 | 2.9 | 300 | 1800 | 1800 | 600
DN25 | 7.5 | 600 | 3609 | 1800 | 800

## Frese STBV-VODRV
QUICK - CALC Frese STBV, VODRV
Setting & Selection program
Input
Input Q: |  | 5000 | (l/h) Flow
Measured diff. Pressure |  | 10 | (kPa) ∆P Signal (For flow measurement)
Kv Signal: (Required) |  | 15.8114
DN | KV signal (Fully open valve) |  | Pre-set |  | KV Total valve |  | Pressureloss (kPa) Total valve (For pump dimensioning)
15 | 6.8 |  | NOT POSSIBLE |  | NOT POSSIBLE |  | NOT POSSIBLE
20 | 9.9 |  | NOT POSSIBLE |  | NOT POSSIBLE |  | NOT POSSIBLE
25 | 31.8 |  | 1.9 |  | 7.378 |  | 45.9264
32 | 23 |  | 2.4 |  | 14.784 |  | 11.4382
40 | 40 |  | 1.6 |  | 13.736 |  | 13.2501
50 | 49.7 |  | 1.3 |  | 15.49 |  | 10.4193
DN 15 |  |  | DN20 |  |  | DN25 |  |  | DN32 |  |  | DN40 |  |  | DN50
KV signal | KV total | Einstellung | KV signal | KV total | Einstellung | KV signal | KV total | Einstellung | KV signal | KV total | Einstellung | KV signal | KV total | Einstellung | KV signal | KV total | Einstellung
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.2 | 0.19 | 0.1 | 0.328 | 0.316 | 0.1 | 0.548 | 0.5 | 0.1 | 0.726 | 0.72 | 0.1 | 0.576 | 0.568 | 0.1 | 1.088 | 1.112 | 0.1
0.4 | 0.38 | 0.2 | 0.656 | 0.632 | 0.2 | 1.096 | 1 | 0.2 | 1.452 | 1.44 | 0.2 | 1.152 | 1.136 | 0.2 | 2.176 | 2.224 | 0.2
0.6 | 0.57 | 0.3 | 0.984 | 0.948 | 0.3 | 1.644 | 1.5 | 0.3 | 2.178 | 2.16 | 0.3 | 1.728 | 1.704 | 0.3 | 3.264 | 3.336 | 0.3
0.8 | 0.76 | 0.4 | 1.312 | 1.264 | 0.4 | 2.192 | 2 | 0.4 | 2.904 | 2.88 | 0.4 | 2.304 | 2.272 | 0.4 | 4.352 | 4.448 | 0.4
1 | 0.95 | 0.5 | 1.64 | 1.58 | 0.5 | 2.74 | 2.5 | 0.5 | 3.63 | 3.6 | 0.5 | 2.88 | 2.84 | 0.5 | 5.44 | 5.56 | 0.5
1.124 | 1.058 | 0.6 | 1.884 | 1.786 | 0.6 | 3.4026 | 2.914 | 0.6 | 4.358 | 4.312 | 0.6 | 3.972 | 3.936 | 0.6 | 6.75 | 6.916 | 0.6
1.248 | 1.166 | 0.7 | 2.128 | 1.992 | 0.7 | 4.0652 | 3.328 | 0.7 | 5.086 | 5.024 | 0.7 | 5.064 | 5.032 | 0.7 | 8.06 | 8.272 | 0.7
1.372 | 1.274 | 0.8 | 2.372 | 2.198 | 0.8 | 4.7278 | 3.742 | 0.8 | 5.814 | 5.736 | 0.8 | 6.156 | 6.128 | 0.8 | 9.37 | 9.628 | 0.8
1.496 | 1.382 | 0.9 | 2.616 | 2.404 | 0.9 | 5.3904 | 4.156 | 0.9 | 6.542 | 6.448 | 0.9 | 7.248 | 7.224 | 0.9 | 10.68 | 10.984 | 0.9
1.62 | 1.49 | 1 | 2.86 | 2.61 | 1 | 6.053 | 4.57 | 1 | 7.27 | 7.16 | 1 | 8.34 | 8.32 | 1 | 11.99 | 12.34 | 1
1.724 | 1.572 | 1.1 | 3.05 | 2.784 | 1.1 | 7.0844 | 4.946 | 1.1 | 8.018 | 7.822 | 1.1 | 9.496 | 9.276 | 1.1 | 13.122 | 13.39 | 1.1
1.828 | 1.654 | 1.2 | 3.24 | 2.958 | 1.2 | 8.1158 | 5.322 | 1.2 | 8.766 | 8.484 | 1.2 | 10.652 | 10.232 | 1.2 | 14.254 | 14.44 | 1.2
1.932 | 1.736 | 1.3 | 3.43 | 3.132 | 1.3 | 9.1472 | 5.698 | 1.3 | 9.514 | 9.146 | 1.3 | 11.808 | 11.188 | 1.3 | 15.386 | 15.49 | 1.3
2.036 | 1.818 | 1.4 | 3.62 | 3.306 | 1.4 | 10.1786 | 6.074 | 1.4 | 10.262 | 9.808 | 1.4 | 12.964 | 12.144 | 1.4 | 16.518 | 16.54 | 1.4
2.14 | 1.9 | 1.5 | 3.81 | 3.48 | 1.5 | 11.21 | 6.45 | 1.5 | 11.01 | 10.47 | 1.5 | 14.12 | 13.1 | 1.5 | 17.65 | 17.59 | 1.5
2.242 | 1.974 | 1.6 | 4.002 | 3.622 | 1.6 | 12.142 | 6.682 | 1.6 | 11.54 | 10.968 | 1.6 | 15.03 | 13.736 | 1.6 | 18.668 | 18.498 | 1.6
2.344 | 2.048 | 1.7 | 4.194 | 3.764 | 1.7 | 13.074 | 6.914 | 1.7 | 12.07 | 11.466 | 1.7 | 15.94 | 14.372 | 1.7 | 19.686 | 19.406 | 1.7
2.446 | 2.122 | 1.8 | 4.386 | 3.906 | 1.8 | 14.006 | 7.146 | 1.8 | 12.6 | 11.964 | 1.8 | 16.85 | 15.008 | 1.8 | 20.704 | 20.314 | 1.8
2.548 | 2.196 | 1.9 | 4.578 | 4.048 | 1.9 | 14.938 | 7.378 | 1.9 | 13.13 | 12.462 | 1.9 | 17.76 | 15.644 | 1.9 | 21.722 | 21.222 | 1.9
2.65 | 2.27 | 2 | 4.77 | 4.19 | 2 | 15.87 | 7.61 | 2 | 13.66 | 12.96 | 2 | 18.67 | 16.28 | 2 | 22.74 | 22.13 | 2
2.698 | 2.316 | 2.1 | 4.92 | 4.324 | 2.1 | 16.838 | 7.828 | 2.1 | 14.132 | 13.416 | 2.1 | 19.542 | 16.87 | 2.1 | 23.766 | 22.834 | 2.1
2.746 | 2.362 | 2.2 | 5.07 | 4.458 | 2.2 | 17.806 | 8.046 | 2.2 | 14.604 | 13.872 | 2.2 | 20.414 | 17.46 | 2.2 | 24.792 | 23.538 | 2.2
2.794 | 2.408 | 2.3 | 5.22 | 4.592 | 2.3 | 18.774 | 8.264 | 2.3 | 15.076 | 14.328 | 2.3 | 21.286 | 18.05 | 2.3 | 25.818 | 24.242 | 2.3
2.842 | 2.454 | 2.4 | 5.37 | 4.726 | 2.4 | 19.742 | 8.482 | 2.4 | 15.548 | 14.784 | 2.4 | 22.158 | 18.64 | 2.4 | 26.844 | 24.946 | 2.4
2.89 | 2.5 | 2.5 | 5.52 | 4.86 | 2.5 | 20.71 | 8.7 | 2.5 | 16.02 | 15.24 | 2.5 | 23.03 | 19.23 | 2.5 | 27.87 | 25.65 | 2.5
3.116 | 2.578 | 2.6 | 5.716 | 4.986 | 2.6 | 21.566 | 8.84 | 2.6 | 16.458 | 15.646 | 2.6 | 23.812 | 19.722 | 2.6 | 28.76 | 26.412 | 2.6
3.342 | 2.656 | 2.7 | 5.912 | 5.112 | 2.7 | 22.422 | 8.98 | 2.7 | 16.896 | 16.052 | 2.7 | 24.594 | 20.214 | 2.7 | 29.65 | 27.174 | 2.7
3.568 | 2.734 | 2.8 | 6.108 | 5.238 | 2.8 | 23.278 | 9.12 | 2.8 | 17.334 | 16.458 | 2.8 | 25.376 | 20.706 | 2.8 | 30.54 | 27.936 | 2.8
3.794 | 2.812 | 2.9 | 6.304 | 5.364 | 2.9 | 24.134 | 9.26 | 2.9 | 17.772 | 16.864 | 2.9 | 26.158 | 21.198 | 2.9 | 31.43 | 28.698 | 2.9
4.02 | 2.89 | 3 | 6.5 | 5.49 | 3 | 24.99 | 9.4 | 3 | 18.21 | 17.27 | 3 | 26.94 | 21.69 | 3 | 32.32 | 29.46 | 3
4.288 | 2.952 | 3.1 | 6.772 | 5.61 | 3.1 | 26.194 | 9.544 | 3.1 | 18.718 | 17.682 | 3.1 | 28.148 | 22.166 | 3.1 | 33.332 | 30.194 | 3.1
4.556 | 3.014 | 3.2 | 7.044 | 5.73 | 3.2 | 27.398 | 9.688 | 3.2 | 19.226 | 18.094 | 3.2 | 29.356 | 22.642 | 3.2 | 34.344 | 30.928 | 3.2
4.824 | 3.076 | 3.3 | 7.316 | 5.85 | 3.3 | 28.602 | 9.832 | 3.3 | 19.734 | 18.506 | 3.3 | 30.564 | 23.118 | 3.3 | 35.356 | 31.662 | 3.3
5.092 | 3.138 | 3.4 | 7.588 | 5.97 | 3.4 | 29.806 | 9.976 | 3.4 | 20.242 | 18.918 | 3.4 | 31.772 | 23.594 | 3.4 | 36.368 | 32.396 | 3.4
5.36 | 3.2 | 3.5 | 7.86 | 6.09 | 3.5 | 31.01 | 10.12 | 3.5 | 20.75 | 19.33 | 3.5 | 32.98 | 24.07 | 3.5 | 37.38 | 33.13 | 3.5
5.648 | 3.258 | 3.6 | 8.264 | 6.172 | 3.6 | 31.166 | 10.196 | 3.6 | 21.202 | 19.664 | 3.6 | 34.374 | 24.456 | 3.6 | 38.444 | 33.768 | 3.6
5.936 | 3.316 | 3.7 | 8.668 | 6.254 | 3.7 | 31.322 | 10.272 | 3.7 | 21.654 | 19.998 | 3.7 | 35.768 | 24.842 | 3.7 | 39.508 | 34.406 | 3.7
6.224 | 3.374 | 3.8 | 9.072 | 6.336 | 3.8 | 31.478 | 10.348 | 3.8 | 22.106 | 20.332 | 3.8 | 37.162 | 25.228 | 3.8 | 40.572 | 35.044 | 3.8
6.512 | 3.432 | 3.9 | 9.476 | 6.418 | 3.9 | 31.634 | 10.424 | 3.9 | 22.558 | 20.666 | 3.9 | 38.556 | 25.614 | 3.9 | 41.636 | 35.682 | 3.9
6.8 | 3.49 | 4 | 9.88 | 6.5 | 4 | 31.79 | 10.5 | 4 | 23.01 | 21 | 4 | 39.95 | 26 | 4 | 42.7 | 36.32 | 4
[15 empty] | 44.1 | 37.056 | 4.1
[15 empty] | 45.5 | 37.792 | 4.2
[15 empty] | 46.9 | 38.528 | 4.3
[15 empty] | 48.3 | 39.264 | 4.4
[15 empty] | 49.7 | 40 | 4.5

## Frese STBV-VODRV flanged
QUICK - CALC Frese STBV, VODRV Flanged
Setting & Selection program
Input
Input Q: |  | 10000 | (l/h) Flow
Measured diff. Pressure |  | 10 | (kPa) Total valve
Kv: (Required) |  | 31.6228
DN | KV (Fully open valve) |  | Pre-set
65 | 64.1139 |  | 2.8
80 | 85.4081 |  | 1.9
100 | 119.2742 |  | 1.3
125 | 202.5046 |  | 0.7
150 | 263.1266 |  | 0.4
200 | 504.3867 |  | 0.2
250 | 911.728 |  | 0.3
300 | 1098.7792 |  | 0.2
350 | 2084.8233 |  | 0.1
400 | 2189.1542 |  | 0.1
450 | 2526.3015 |  | 0.1
500 | 3381.0933 |  | 0
DN65 |  | DN80 |  | DN100 |  | DN125 |  | DN150 |  | DN200 |  | DN250 |  | DN300 |  | DN350 |  | DN400 |  | DN450 |  | DN500
KV | Einstellung | KV | Einstellung | KV | Einstellung | KV | Einstellung | KV | Einstellung | KV | Einstellung | KV | Einstellung | KV | Einstellung | KV | Einstellung | KV | Einstellung | KV | Einstellung | KV | Einstellung
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.6813 | 0.1 | 1.6827 | 0.1 | 2.5113 | 0.1 | 3.9673 | 0.1 | 7.7206 | 0.1 | 13.4068 | 0.1 | 10.4302 | 0.1 | 12.9601 | 0.1 | 16.8991 | 0.1 | 23.2404 | 0.1 | 25.4536 | 0.1 | 32.1578 | 0.1
3.3625 | 0.2 | 3.3654 | 0.2 | 5.0226 | 0.2 | 7.9347 | 0.2 | 15.4411 | 0.2 | 26.8137 | 0.2 | 20.8604 | 0.2 | 25.9202 | 0.2 | 33.7981 | 0.2 | 46.4808 | 0.2 | 50.9073 | 0.2 | 64.3155 | 0.2
5.0438 | 0.3 | 5.0481 | 0.3 | 7.5339 | 0.3 | 11.902 | 0.3 | 23.1617 | 0.3 | 40.2205 | 0.3 | 31.2906 | 0.3 | 38.8804 | 0.3 | 50.6972 | 0.3 | 69.7212 | 0.3 | 76.3609 | 0.3 | 96.4733 | 0.3
6.7251 | 0.4 | 6.7308 | 0.4 | 10.0452 | 0.4 | 15.8694 | 0.4 | 30.8823 | 0.4 | 53.6273 | 0.4 | 41.7208 | 0.4 | 51.8405 | 0.4 | 67.5963 | 0.4 | 92.9616 | 0.4 | 101.8145 | 0.4 | 128.6311 | 0.4
8.4064 | 0.5 | 8.4136 | 0.5 | 12.5565 | 0.5 | 19.8367 | 0.5 | 38.6028 | 0.5 | 67.0341 | 0.5 | 52.151 | 0.5 | 64.8006 | 0.5 | 84.4954 | 0.5 | 116.202 | 0.5 | 127.2681 | 0.5 | 160.7888 | 0.5
10.0876 | 0.6 | 10.0963 | 0.6 | 15.0678 | 0.6 | 23.804 | 0.6 | 46.3234 | 0.6 | 80.441 | 0.6 | 62.5811 | 0.6 | 77.7607 | 0.6 | 101.3944 | 0.6 | 139.4424 | 0.6 | 152.7218 | 0.6 | 192.9466 | 0.6
11.7689 | 0.7 | 11.779 | 0.7 | 17.579 | 0.7 | 27.7714 | 0.7 | 54.044 | 0.7 | 93.8478 | 0.7 | 73.0113 | 0.7 | 90.7209 | 0.7 | 118.2935 | 0.7 | 162.6828 | 0.7 | 178.1754 | 0.7 | 225.1044 | 0.7
13.4502 | 0.8 | 13.4617 | 0.8 | 20.0903 | 0.8 | 31.7387 | 0.8 | 61.7645 | 0.8 | 107.2546 | 0.8 | 83.4415 | 0.8 | 103.681 | 0.8 | 135.1926 | 0.8 | 185.9232 | 0.8 | 203.629 | 0.8 | 257.2621 | 0.8
15.1314 | 0.9 | 15.1444 | 0.9 | 22.6016 | 0.9 | 35.7061 | 0.9 | 69.4851 | 0.9 | 120.6615 | 0.9 | 93.8717 | 0.9 | 116.6411 | 0.9 | 152.0916 | 0.9 | 209.1636 | 0.9 | 229.0826 | 0.9 | 289.4199 | 0.9
16.8127 | 1 | 16.8271 | 1 | 25.1129 | 1 | 39.6734 | 1 | 77.2057 | 1 | 134.0683 | 1 | 104.3019 | 1 | 129.6012 | 1 | 168.9907 | 1 | 232.404 | 1 | 254.5363 | 1 | 321.5777 | 1
17.6505 | 1.1 | 18.3266 | 1.1 | 26.9914 | 1.1 | 42.4793 | 1.1 | 81.1196 | 1.1 | 138.8057 | 1.1 | 109.4093 | 1.1 | 138.3336 | 1.1 | 181.8949 | 1.1 | 247.5387 | 1.1 | 269.2989 | 1.1 | 345.9495 | 1.1
18.4883 | 1.2 | 19.826 | 1.2 | 28.8698 | 1.2 | 45.2852 | 1.2 | 85.0335 | 1.2 | 143.5432 | 1.2 | 114.5168 | 1.2 | 147.066 | 1.2 | 194.7992 | 1.2 | 262.6734 | 1.2 | 284.0616 | 1.2 | 370.3214 | 1.2
19.3261 | 1.3 | 21.3255 | 1.3 | 30.7483 | 1.3 | 48.0911 | 1.3 | 88.9475 | 1.3 | 148.2806 | 1.3 | 119.6242 | 1.3 | 155.7983 | 1.3 | 207.7034 | 1.3 | 277.8082 | 1.3 | 298.8242 | 1.3 | 394.6933 | 1.3
20.1639 | 1.4 | 22.8249 | 1.4 | 32.6267 | 1.4 | 50.897 | 1.4 | 92.8614 | 1.4 | 153.018 | 1.4 | 124.7316 | 1.4 | 164.5307 | 1.4 | 220.6076 | 1.4 | 292.9429 | 1.4 | 313.5869 | 1.4 | 419.0652 | 1.4
21.0017 | 1.5 | 24.3244 | 1.5 | 34.5052 | 1.5 | 53.7029 | 1.5 | 96.7753 | 1.5 | 157.7555 | 1.5 | 129.839 | 1.5 | 173.2631 | 1.5 | 233.5119 | 1.5 | 308.0776 | 1.5 | 328.3495 | 1.5 | 443.437 | 1.5
21.8396 | 1.6 | 25.8238 | 1.6 | 36.3836 | 1.6 | 56.5088 | 1.6 | 100.6893 | 1.6 | 162.4929 | 1.6 | 134.9465 | 1.6 | 181.9954 | 1.6 | 246.4161 | 1.6 | 323.2123 | 1.6 | 343.1122 | 1.6 | 467.8089 | 1.6
22.6774 | 1.7 | 27.3233 | 1.7 | 38.2621 | 1.7 | 59.3147 | 1.7 | 104.6032 | 1.7 | 167.2303 | 1.7 | 140.0539 | 1.7 | 190.7278 | 1.7 | 259.3203 | 1.7 | 338.347 | 1.7 | 357.8749 | 1.7 | 492.1808 | 1.7
23.5152 | 1.8 | 28.8227 | 1.8 | 40.1405 | 1.8 | 62.1206 | 1.8 | 108.5172 | 1.8 | 171.9678 | 1.8 | 145.1613 | 1.8 | 199.4602 | 1.8 | 272.2246 | 1.8 | 353.4817 | 1.8 | 372.6375 | 1.8 | 516.5527 | 1.8
24.353 | 1.9 | 30.3222 | 1.9 | 42.019 | 1.9 | 64.9265 | 1.9 | 112.4311 | 1.9 | 176.7052 | 1.9 | 150.2687 | 1.9 | 208.1925 | 1.9 | 285.1288 | 1.9 | 368.6165 | 1.9 | 387.4002 | 1.9 | 540.9245 | 1.9
25.1908 | 2 | 31.8216 | 2 | 43.8975 | 2 | 67.7324 | 2 | 116.345 | 2 | 181.4426 | 2 | 155.3762 | 2 | 216.9249 | 2 | 298.033 | 2 | 383.7512 | 2 | 402.1628 | 2 | 565.2964 | 2
25.9802 | 2.1 | 32.6971 | 2.1 | 45.4598 | 2.1 | 70.2834 | 2.1 | 119.4408 | 2.1 | 185.226 | 2.1 | 163.0773 | 2.1 | 224.7888 | 2.1 | 311.5089 | 2.1 | 398.0993 | 2.1 | 418.4651 | 2.1 | 587.152 | 2.1
26.7697 | 2.2 | 33.5726 | 2.2 | 47.0221 | 2.2 | 72.8344 | 2.2 | 122.5367 | 2.2 | 189.0094 | 2.2 | 170.7785 | 2.2 | 232.6527 | 2.2 | 324.9848 | 2.2 | 412.4474 | 2.2 | 434.7673 | 2.2 | 609.0076 | 2.2
27.5592 | 2.3 | 34.448 | 2.3 | 48.5844 | 2.3 | 75.3854 | 2.3 | 125.6325 | 2.3 | 192.7928 | 2.3 | 178.4796 | 2.3 | 240.5166 | 2.3 | 338.4607 | 2.3 | 426.7956 | 2.3 | 451.0696 | 2.3 | 630.8633 | 2.3
28.3486 | 2.4 | 35.3235 | 2.4 | 50.1468 | 2.4 | 77.9364 | 2.4 | 128.7283 | 2.4 | 196.5762 | 2.4 | 186.1807 | 2.4 | 248.3805 | 2.4 | 351.9366 | 2.4 | 441.1437 | 2.4 | 467.3719 | 2.4 | 652.7189 | 2.4
29.1381 | 2.5 | 36.199 | 2.5 | 51.7091 | 2.5 | 80.4874 | 2.5 | 131.8241 | 2.5 | 200.3597 | 2.5 | 193.8819 | 2.5 | 256.2444 | 2.5 | 365.4125 | 2.5 | 455.4918 | 2.5 | 483.6741 | 2.5 | 674.5745 | 2.5
29.9276 | 2.6 | 37.0744 | 2.6 | 53.2714 | 2.6 | 83.0384 | 2.6 | 134.9199 | 2.6 | 204.1431 | 2.6 | 201.583 | 2.6 | 264.1083 | 2.6 | 378.8884 | 2.6 | 469.8399 | 2.6 | 499.9764 | 2.6 | 696.4301 | 2.6
30.717 | 2.7 | 37.9499 | 2.7 | 54.8338 | 2.7 | 85.5894 | 2.7 | 138.0157 | 2.7 | 207.9265 | 2.7 | 209.2842 | 2.7 | 271.9722 | 2.7 | 392.3643 | 2.7 | 484.1881 | 2.7 | 516.2786 | 2.7 | 718.2858 | 2.7
31.5065 | 2.8 | 38.8254 | 2.8 | 56.3961 | 2.8 | 88.1404 | 2.8 | 141.1116 | 2.8 | 211.7099 | 2.8 | 216.9853 | 2.8 | 279.8361 | 2.8 | 405.8402 | 2.8 | 498.5362 | 2.8 | 532.5809 | 2.8 | 740.1414 | 2.8
32.296 | 2.9 | 39.7008 | 2.9 | 57.9584 | 2.9 | 90.6914 | 2.9 | 144.2074 | 2.9 | 215.4933 | 2.9 | 224.6864 | 2.9 | 287.7 | 2.9 | 419.3161 | 2.9 | 512.8843 | 2.9 | 548.8832 | 2.9 | 761.997 | 2.9
33.0854 | 3 | 40.5763 | 3 | 59.5207 | 3 | 93.2424 | 3 | 147.3032 | 3 | 219.2767 | 3 | 232.3876 | 3 | 295.5638 | 3 | 432.792 | 3 | 527.2324 | 3 | 565.1854 | 3 | 783.8526 | 3
33.5191 | 3.1 | 41.3068 | 3.1 | 60.971 | 3.1 | 95.3369 | 3.1 | 150.3589 | 3.1 | 221.4227 | 3.1 | 238.2836 | 3.1 | 302.9298 | 3.1 | 444.7623 | 3.1 | 541.2176 | 3.1 | 581.867 | 3.1 | 804.5787 | 3.1
33.9528 | 3.2 | 42.0372 | 3.2 | 62.4213 | 3.2 | 97.4314 | 3.2 | 153.4146 | 3.2 | 223.5686 | 3.2 | 244.1796 | 3.2 | 310.2958 | 3.2 | 456.7326 | 3.2 | 555.2027 | 3.2 | 598.5486 | 3.2 | 825.3048 | 3.2
34.3866 | 3.3 | 42.7676 | 3.3 | 63.8716 | 3.3 | 99.5259 | 3.3 | 156.4702 | 3.3 | 225.7146 | 3.3 | 250.0756 | 3.3 | 317.6618 | 3.3 | 468.7028 | 3.3 | 569.1879 | 3.3 | 615.2301 | 3.3 | 846.0308 | 3.3
34.8203 | 3.4 | 43.4981 | 3.4 | 65.3219 | 3.4 | 101.6204 | 3.4 | 159.5259 | 3.4 | 227.8606 | 3.4 | 255.9717 | 3.4 | 325.0278 | 3.4 | 480.6731 | 3.4 | 583.173 | 3.4 | 631.9117 | 3.4 | 866.7569 | 3.4
35.254 | 3.5 | 44.2285 | 3.5 | 66.7722 | 3.5 | 103.715 | 3.5 | 162.5816 | 3.5 | 230.0066 | 3.5 | 261.8677 | 3.5 | 332.3938 | 3.5 | 492.6434 | 3.5 | 597.1582 | 3.5 | 648.5933 | 3.5 | 887.483 | 3.5
35.6877 | 3.6 | 44.959 | 3.6 | 68.2224 | 3.6 | 105.8095 | 3.6 | 165.6373 | 3.6 | 232.1526 | 3.6 | 267.7637 | 3.6 | 339.7598 | 3.6 | 504.6136 | 3.6 | 611.1433 | 3.6 | 665.2748 | 3.6 | 908.209 | 3.6
36.1214 | 3.7 | 45.6894 | 3.7 | 69.6727 | 3.7 | 107.904 | 3.7 | 168.693 | 3.7 | 234.2985 | 3.7 | 273.6597 | 3.7 | 347.1258 | 3.7 | 516.5839 | 3.7 | 625.1285 | 3.7 | 681.9564 | 3.7 | 928.9351 | 3.7
36.5551 | 3.8 | 46.4199 | 3.8 | 71.123 | 3.8 | 109.9985 | 3.8 | 171.7487 | 3.8 | 236.4445 | 3.8 | 279.5557 | 3.8 | 354.4918 | 3.8 | 528.5542 | 3.8 | 639.1136 | 3.8 | 698.638 | 3.8 | 949.6612 | 3.8
36.9888 | 3.9 | 47.1503 | 3.9 | 72.5733 | 3.9 | 112.093 | 3.9 | 174.8044 | 3.9 | 238.5905 | 3.9 | 285.4518 | 3.9 | 361.8578 | 3.9 | 540.5244 | 3.9 | 653.0987 | 3.9 | 715.3195 | 3.9 | 970.3872 | 3.9
37.4225 | 4 | 47.8808 | 4 | 74.0236 | 4 | 114.1875 | 4 | 177.8601 | 4 | 240.7365 | 4 | 291.3478 | 4 | 369.2238 | 4 | 552.4947 | 4 | 667.0839 | 4 | 732.0011 | 4 | 991.1133 | 4
37.8955 | 4.1 | 48.7487 | 4.1 | 75.0305 | 4.1 | 115.8509 | 4.1 | 180.529 | 4.1 | 242.7062 | 4.1 | 297.2556 | 4.1 | 375.3299 | 4.1 | 565.0749 | 4.1 | 680.1528 | 4.1 | 746.04 | 4.1 | 1010.831 | 4.1
38.3686 | 4.2 | 49.6167 | 4.2 | 76.0375 | 4.2 | 117.5143 | 4.2 | 183.1979 | 4.2 | 244.6758 | 4.2 | 303.1635 | 4.2 | 381.4359 | 4.2 | 577.655 | 4.2 | 693.2217 | 4.2 | 760.0789 | 4.2 | 1030.5486 | 4.2
38.8416 | 4.3 | 50.4847 | 4.3 | 77.0444 | 4.3 | 119.1777 | 4.3 | 185.8668 | 4.3 | 246.6455 | 4.3 | 309.0713 | 4.3 | 387.5419 | 4.3 | 590.2351 | 4.3 | 706.2906 | 4.3 | 774.1178 | 4.3 | 1050.2663 | 4.3
39.3146 | 4.4 | 51.3527 | 4.4 | 78.0513 | 4.4 | 120.8411 | 4.4 | 188.5357 | 4.4 | 248.6152 | 4.4 | 314.9792 | 4.4 | 393.6479 | 4.4 | 602.8153 | 4.4 | 719.3594 | 4.4 | 788.1568 | 4.4 | 1069.9839 | 4.4
39.7876 | 4.5 | 52.2207 | 4.5 | 79.0583 | 4.5 | 122.5046 | 4.5 | 191.2047 | 4.5 | 250.5849 | 4.5 | 320.887 | 4.5 | 399.7539 | 4.5 | 615.3954 | 4.5 | 732.4283 | 4.5 | 802.1957 | 4.5 | 1089.7016 | 4.5
40.2607 | 4.6 | 53.0887 | 4.6 | 80.0652 | 4.6 | 124.168 | 4.6 | 193.8736 | 4.6 | 252.5546 | 4.6 | 326.7948 | 4.6 | 405.86 | 4.6 | 627.9756 | 4.6 | 745.4972 | 4.6 | 816.2346 | 4.6 | 1109.4193 | 4.6
40.7337 | 4.7 | 53.9567 | 4.7 | 81.0722 | 4.7 | 125.8314 | 4.7 | 196.5425 | 4.7 | 254.5243 | 4.7 | 332.7027 | 4.7 | 411.966 | 4.7 | 640.5557 | 4.7 | 758.5661 | 4.7 | 830.2735 | 4.7 | 1129.1369 | 4.7
41.2067 | 4.8 | 54.8247 | 4.8 | 82.0791 | 4.8 | 127.4948 | 4.8 | 199.2114 | 4.8 | 256.4939 | 4.8 | 338.6105 | 4.8 | 418.072 | 4.8 | 653.1359 | 4.8 | 771.635 | 4.8 | 844.3124 | 4.8 | 1148.8546 | 4.8
41.6798 | 4.9 | 55.6926 | 4.9 | 83.0861 | 4.9 | 129.1582 | 4.9 | 201.8804 | 4.9 | 258.4636 | 4.9 | 344.5184 | 4.9 | 424.178 | 4.9 | 665.716 | 4.9 | 784.7039 | 4.9 | 858.3513 | 4.9 | 1168.5723 | 4.9
42.1528 | 5 | 56.5606 | 5 | 84.093 | 5 | 130.8216 | 5 | 204.5493 | 5 | 260.4333 | 5 | 350.4262 | 5 | 430.2841 | 5 | 678.2962 | 5 | 797.7728 | 5 | 872.3902 | 5 | 1188.2899 | 5
42.9191 | 5.1 | 57.5061 | 5.1 | 85.2349 | 5.1 | 133.3249 | 5.1 | 206.9476 | 5.1 | 263.4643 | 5.1 | 356.5787 | 5.1 | 436.8331 | 5.1 | 688.2255 | 5.1 | 808.4162 | 5.1 | 887.4938 | 5.1 | 1206.1978 | 5.1
43.6855 | 5.2 | 58.4515 | 5.2 | 86.3768 | 5.2 | 135.8282 | 5.2 | 209.346 | 5.2 | 266.4952 | 5.2 | 362.7311 | 5.2 | 443.3821 | 5.2 | 698.1548 | 5.2 | 819.0596 | 5.2 | 902.5975 | 5.2 | 1224.1056 | 5.2
44.4518 | 5.3 | 59.3969 | 5.3 | 87.5187 | 5.3 | 138.3315 | 5.3 | 211.7443 | 5.3 | 269.5262 | 5.3 | 368.8836 | 5.3 | 449.9311 | 5.3 | 708.0841 | 5.3 | 829.703 | 5.3 | 917.7011 | 5.3 | 1242.0135 | 5.3
45.2182 | 5.4 | 60.3423 | 5.4 | 88.6606 | 5.4 | 140.8349 | 5.4 | 214.1427 | 5.4 | 272.5572 | 5.4 | 375.036 | 5.4 | 456.4801 | 5.4 | 718.0134 | 5.4 | 840.3464 | 5.4 | 932.8047 | 5.4 | 1259.9213 | 5.4
45.9845 | 5.5 | 61.2877 | 5.5 | 89.8024 | 5.5 | 143.3382 | 5.5 | 216.541 | 5.5 | 275.5881 | 5.5 | 381.1885 | 5.5 | 463.0291 | 5.5 | 727.9427 | 5.5 | 850.9898 | 5.5 | 947.9083 | 5.5 | 1277.8292 | 5.5
46.7509 | 5.6 | 62.2332 | 5.6 | 90.9443 | 5.6 | 145.8415 | 5.6 | 218.9394 | 5.6 | 278.6191 | 5.6 | 387.341 | 5.6 | 469.5781 | 5.6 | 737.872 | 5.6 | 861.6332 | 5.6 | 963.012 | 5.6 | 1295.737 | 5.6
47.5172 | 5.7 | 63.1786 | 5.7 | 92.0862 | 5.7 | 148.3448 | 5.7 | 221.3377 | 5.7 | 281.65 | 5.7 | 393.4934 | 5.7 | 476.1271 | 5.7 | 747.8013 | 5.7 | 872.2766 | 5.7 | 978.1156 | 5.7 | 1313.6448 | 5.7
48.2836 | 5.8 | 64.124 | 5.8 | 93.2281 | 5.8 | 150.8481 | 5.8 | 223.7361 | 5.8 | 284.681 | 5.8 | 399.6459 | 5.8 | 482.6761 | 5.8 | 757.7306 | 5.8 | 882.92 | 5.8 | 993.2192 | 5.8 | 1331.5527 | 5.8
49.0499 | 5.9 | 65.0694 | 5.9 | 94.37 | 5.9 | 153.3514 | 5.9 | 226.1344 | 5.9 | 287.712 | 5.9 | 405.7983 | 5.9 | 489.2251 | 5.9 | 767.6599 | 5.9 | 893.5633 | 5.9 | 1008.3228 | 5.9 | 1349.4605 | 5.9
49.8162 | 6 | 66.0148 | 6 | 95.5119 | 6 | 155.8547 | 6 | 228.5327 | 6 | 290.7429 | 6 | 411.9508 | 6 | 495.7742 | 6 | 777.5892 | 6 | 904.2067 | 6 | 1023.4265 | 6 | 1367.3684 | 6
50.6566 | 6.1 | 67.0073 | 6.1 | 96.7313 | 6.1 | 158.321 | 6.1 | 230.5761 | 6.1 | 294.182 | 6.1 | 417.0726 | 6.1 | 503.3833 | 6.1 | 786.8066 | 6.1 | 913.4261 | 6.1 | 1035.2657 | 6.1 | 1380.8412 | 6.1
51.4969 | 6.2 | 67.9997 | 6.2 | 97.9507 | 6.2 | 160.7873 | 6.2 | 232.6195 | 6.2 | 297.621 | 6.2 | 422.1944 | 6.2 | 510.9924 | 6.2 | 796.024 | 6.2 | 922.6455 | 6.2 | 1047.105 | 6.2 | 1394.314 | 6.2
52.3373 | 6.3 | 68.9922 | 6.3 | 99.1702 | 6.3 | 163.2536 | 6.3 | 234.6629 | 6.3 | 301.06 | 6.3 | 427.3163 | 6.3 | 518.6015 | 6.3 | 805.2414 | 6.3 | 931.8648 | 6.3 | 1058.9443 | 6.3 | 1407.7869 | 6.3
53.1776 | 6.4 | 69.9846 | 6.4 | 100.3896 | 6.4 | 165.7199 | 6.4 | 236.7062 | 6.4 | 304.4991 | 6.4 | 432.4381 | 6.4 | 526.2106 | 6.4 | 814.4588 | 6.4 | 941.0842 | 6.4 | 1070.7836 | 6.4 | 1421.2597 | 6.4
54.0179 | 6.5 | 70.977 | 6.5 | 101.6091 | 6.5 | 168.1862 | 6.5 | 238.7496 | 6.5 | 307.9381 | 6.5 | 437.5599 | 6.5 | 533.8197 | 6.5 | 823.6762 | 6.5 | 950.3036 | 6.5 | 1082.6229 | 6.5 | 1434.7325 | 6.5
54.8583 | 6.6 | 71.9695 | 6.6 | 102.8285 | 6.6 | 170.6525 | 6.6 | 240.793 | 6.6 | 311.3771 | 6.6 | 442.6817 | 6.6 | 541.4288 | 6.6 | 832.8936 | 6.6 | 959.5229 | 6.6 | 1094.4622 | 6.6 | 1448.2053 | 6.6
55.6986 | 6.7 | 72.9619 | 6.7 | 104.048 | 6.7 | 173.1188 | 6.7 | 242.8364 | 6.7 | 314.8161 | 6.7 | 447.8036 | 6.7 | 549.0379 | 6.7 | 842.111 | 6.7 | 968.7423 | 6.7 | 1106.3014 | 6.7 | 1461.6781 | 6.7
56.5389 | 6.8 | 73.9544 | 6.8 | 105.2674 | 6.8 | 175.5851 | 6.8 | 244.8797 | 6.8 | 318.2552 | 6.8 | 452.9254 | 6.8 | 556.647 | 6.8 | 851.3284 | 6.8 | 977.9616 | 6.8 | 1118.1407 | 6.8 | 1475.151 | 6.8
57.3793 | 6.9 | 74.9468 | 6.9 | 106.4868 | 6.9 | 178.0514 | 6.9 | 246.9231 | 6.9 | 321.6942 | 6.9 | 458.0472 | 6.9 | 564.2561 | 6.9 | 860.5458 | 6.9 | 987.181 | 6.9 | 1129.98 | 6.9 | 1488.6238 | 6.9
58.2196 | 7 | 75.9392 | 7 | 107.7063 | 7 | 180.5177 | 7 | 248.9665 | 7 | 325.1332 | 7 | 463.169 | 7 | 571.8652 | 7 | 869.7632 | 7 | 996.4004 | 7 | 1141.8193 | 7 | 1502.0966 | 7
58.809 | 7.1 | 76.8861 | 7.1 | 108.8631 | 7.1 | 182.7164 | 7.1 | 250.3825 | 7.1 | 329.0757 | 7.1 | 466.1781 | 7.1 | 578.6914 | 7.1 | 878.1781 | 7.1 | 1004.7412 | 7.1 | 1155.5018 | 7.1 | 1512.7934 | 7.1
59.3985 | 7.2 | 77.833 | 7.2 | 110.0199 | 7.2 | 184.9151 | 7.2 | 251.7985 | 7.2 | 333.0182 | 7.2 | 469.1871 | 7.2 | 585.5177 | 7.2 | 886.5931 | 7.2 | 1013.0821 | 7.2 | 1169.1844 | 7.2 | 1523.4903 | 7.2
59.9879 | 7.3 | 78.7799 | 7.3 | 111.1767 | 7.3 | 187.1138 | 7.3 | 253.2145 | 7.3 | 336.9606 | 7.3 | 472.1962 | 7.3 | 592.3439 | 7.3 | 895.008 | 7.3 | 1021.423 | 7.3 | 1182.8669 | 7.3 | 1534.1871 | 7.3
60.5773 | 7.4 | 79.7268 | 7.4 | 112.3334 | 7.4 | 189.3125 | 7.4 | 254.6305 | 7.4 | 340.9031 | 7.4 | 475.2053 | 7.4 | 599.1701 | 7.4 | 903.4229 | 7.4 | 1029.7639 | 7.4 | 1196.5495 | 7.4 | 1544.8839 | 7.4
61.1667 | 7.5 | 80.6737 | 7.5 | 113.4902 | 7.5 | 191.5111 | 7.5 | 256.0465 | 7.5 | 344.8456 | 7.5 | 478.2143 | 7.5 | 605.9963 | 7.5 | 911.8379 | 7.5 | 1038.1047 | 7.5 | 1210.2321 | 7.5 | 1555.5807 | 7.5
61.7562 | 7.6 | 81.6206 | 7.6 | 114.647 | 7.6 | 193.7098 | 7.6 | 257.4625 | 7.6 | 348.7881 | 7.6 | 481.2234 | 7.6 | 612.8226 | 7.6 | 920.2528 | 7.6 | 1046.4456 | 7.6 | 1223.9146 | 7.6 | 1566.2776 | 7.6
62.3456 | 7.7 | 82.5674 | 7.7 | 115.8038 | 7.7 | 195.9085 | 7.7 | 258.8785 | 7.7 | 352.7305 | 7.7 | 484.2324 | 7.7 | 619.6488 | 7.7 | 928.6678 | 7.7 | 1054.7865 | 7.7 | 1237.5972 | 7.7 | 1576.9744 | 7.7
62.935 | 7.8 | 83.5143 | 7.8 | 116.9606 | 7.8 | 198.1072 | 7.8 | 260.2946 | 7.8 | 356.673 | 7.8 | 487.2415 | 7.8 | 626.475 | 7.8 | 937.0827 | 7.8 | 1063.1274 | 7.8 | 1251.2797 | 7.8 | 1587.6712 | 7.8
63.5245 | 7.9 | 84.4612 | 7.9 | 118.1174 | 7.9 | 200.3059 | 7.9 | 261.7106 | 7.9 | 360.6155 | 7.9 | 490.2505 | 7.9 | 633.3012 | 7.9 | 945.4976 | 7.9 | 1071.4682 | 7.9 | 1264.9623 | 7.9 | 1598.368 | 7.9
64.1139 | 8 | 85.4081 | 8 | 119.2742 | 8 | 202.5046 | 8 | 263.1266 | 8 | 364.558 | 8 | 493.2596 | 8 | 640.1274 | 8 | 953.9126 | 8 | 1079.8091 | 8 | 1278.6448 | 8 | 1609.0649 | 8
[10 empty] | 368.5717 | 8.1 | 497.0464 | 8.1 | 646.6795 | 8.1 | 959.0791 | 8.1 | 1083.8874 | 8.1 | 1284.3629 | 8.1 | 1618.2765 | 8.1
[10 empty] | 372.5854 | 8.2 | 500.8332 | 8.2 | 653.2316 | 8.2 | 964.2455 | 8.2 | 1087.9657 | 8.2 | 1290.081 | 8.2 | 1627.4881 | 8.2
[10 empty] | 376.5992 | 8.3 | 504.62 | 8.3 | 659.7837 | 8.3 | 969.412 | 8.3 | 1092.044 | 8.3 | 1295.7991 | 8.3 | 1636.6997 | 8.3
[10 empty] | 380.6129 | 8.4 | 508.4068 | 8.4 | 666.3357 | 8.4 | 974.5785 | 8.4 | 1096.1223 | 8.4 | 1301.5172 | 8.4 | 1645.9113 | 8.4
[10 empty] | 384.6267 | 8.5 | 512.1936 | 8.5 | 672.8878 | 8.5 | 979.7449 | 8.5 | 1100.2006 | 8.5 | 1307.2353 | 8.5 | 1655.1229 | 8.5
[10 empty] | 388.6404 | 8.6 | 515.9804 | 8.6 | 679.4399 | 8.6 | 984.9114 | 8.6 | 1104.2789 | 8.6 | 1312.9533 | 8.6 | 1664.3345 | 8.6
[10 empty] | 392.6541 | 8.7 | 519.7672 | 8.7 | 685.992 | 8.7 | 990.0779 | 8.7 | 1108.3572 | 8.7 | 1318.6714 | 8.7 | 1673.5461 | 8.7
[10 empty] | 396.6679 | 8.8 | 523.554 | 8.8 | 692.544 | 8.8 | 995.2444 | 8.8 | 1112.4355 | 8.8 | 1324.3895 | 8.8 | 1682.7577 | 8.8
[10 empty] | 400.6816 | 8.9 | 527.3408 | 8.9 | 699.0961 | 8.9 | 1000.4108 | 8.9 | 1116.5138 | 8.9 | 1330.1076 | 8.9 | 1691.9693 | 8.9
[10 empty] | 404.6953 | 9 | 531.1276 | 9 | 705.6482 | 9 | 1005.5773 | 9 | 1120.5921 | 9 | 1335.8257 | 9 | 1701.1809 | 9
[10 empty] | 409.1841 | 9.1 | 536.3135 | 9.1 | 710.0286 | 9.1 | 1007.8488 | 9.1 | 1122.9188 | 9.1 | 1346.502 | 9.1 | 1706.3701 | 9.1
[10 empty] | 413.673 | 9.2 | 541.4994 | 9.2 | 714.409 | 9.2 | 1010.1202 | 9.2 | 1125.2455 | 9.2 | 1357.1783 | 9.2 | 1711.5593 | 9.2
[10 empty] | 418.1618 | 9.3 | 546.6853 | 9.3 | 718.7894 | 9.3 | 1012.3917 | 9.3 | 1127.5722 | 9.3 | 1367.8546 | 9.3 | 1716.7485 | 9.3
[10 empty] | 422.6506 | 9.4 | 551.8712 | 9.4 | 723.1698 | 9.4 | 1014.6631 | 9.4 | 1129.8989 | 9.4 | 1378.531 | 9.4 | 1721.9377 | 9.4
[10 empty] | 427.1394 | 9.5 | 557.0571 | 9.5 | 727.5503 | 9.5 | 1016.9346 | 9.5 | 1132.2256 | 9.5 | 1389.2073 | 9.5 | 1727.1269 | 9.5
[10 empty] | 431.6282 | 9.6 | 562.243 | 9.6 | 731.9307 | 9.6 | 1019.206 | 9.6 | 1134.5523 | 9.6 | 1399.8836 | 9.6 | 1732.3161 | 9.6
[10 empty] | 436.117 | 9.7 | 567.4289 | 9.7 | 736.3111 | 9.7 | 1021.4775 | 9.7 | 1136.879 | 9.7 | 1410.5599 | 9.7 | 1737.5053 | 9.7
[10 empty] | 440.6058 | 9.8 | 572.6148 | 9.8 | 740.6915 | 9.8 | 1023.7489 | 9.8 | 1139.2057 | 9.8 | 1421.2363 | 9.8 | 1742.6945 | 9.8
[10 empty] | 445.0946 | 9.9 | 577.8007 | 9.9 | 745.0719 | 9.9 | 1026.0204 | 9.9 | 1141.5324 | 9.9 | 1431.9126 | 9.9 | 1747.8837 | 9.9
[10 empty] | 449.5835 | 10 | 582.9866 | 10 | 749.4523 | 10 | 1028.2918 | 10 | 1143.8591 | 10 | 1442.5889 | 10 | 1753.0729 | 10
[10 empty] | 453.2484 | 10.1 | 587.0872 | 10.1 | 750.9872 | 10.1 | 1037.7459 | 10.1 | 1146.9471 | 10.1 | 1454.0802 | 10.1 | 1756.6543 | 10.1
[10 empty] | 456.9134 | 10.2 | 591.1879 | 10.2 | 752.522 | 10.2 | 1047.2 | 10.2 | 1150.0352 | 10.2 | 1465.5714 | 10.2 | 1760.2358 | 10.2
[10 empty] | 460.5783 | 10.3 | 595.2886 | 10.3 | 754.0568 | 10.3 | 1056.654 | 10.3 | 1153.1232 | 10.3 | 1477.0627 | 10.3 | 1763.8172 | 10.3
[10 empty] | 464.2433 | 10.4 | 599.3893 | 10.4 | 755.5916 | 10.4 | 1066.1081 | 10.4 | 1156.2113 | 10.4 | 1488.554 | 10.4 | 1767.3986 | 10.4
[10 empty] | 467.9083 | 10.5 | 603.4899 | 10.5 | 757.1264 | 10.5 | 1075.5622 | 10.5 | 1159.2993 | 10.5 | 1500.0452 | 10.5 | 1770.98 | 10.5
[10 empty] | 471.5732 | 10.6 | 607.5906 | 10.6 | 758.6612 | 10.6 | 1085.0162 | 10.6 | 1162.3873 | 10.6 | 1511.5365 | 10.6 | 1774.5615 | 10.6
[10 empty] | 475.2382 | 10.7 | 611.6913 | 10.7 | 760.1961 | 10.7 | 1094.4703 | 10.7 | 1165.4754 | 10.7 | 1523.0277 | 10.7 | 1778.1429 | 10.7
[10 empty] | 478.9032 | 10.8 | 615.7919 | 10.8 | 761.7309 | 10.8 | 1103.9243 | 10.8 | 1168.5634 | 10.8 | 1534.519 | 10.8 | 1781.7243 | 10.8
[10 empty] | 482.5681 | 10.9 | 619.8926 | 10.9 | 763.2657 | 10.9 | 1113.3784 | 10.9 | 1171.6514 | 10.9 | 1546.0103 | 10.9 | 1785.3057 | 10.9
[10 empty] | 486.2331 | 11 | 623.9933 | 11 | 764.8005 | 11 | 1122.8325 | 11 | 1174.7395 | 11 | 1557.5015 | 11 | 1788.8871 | 11
[10 empty] | 488.0484 | 11.1 | 629.5048 | 11.1 | 769.3564 | 11.1 | 1136.1469 | 11.1 | 1184.2658 | 11.1 | 1559.6441 | 11.1 | 1802.1741 | 11.1
[10 empty] | 489.8638 | 11.2 | 635.0162 | 11.2 | 773.9124 | 11.2 | 1149.4613 | 11.2 | 1193.7922 | 11.2 | 1561.7868 | 11.2 | 1815.461 | 11.2
[10 empty] | 491.6792 | 11.3 | 640.5277 | 11.3 | 778.4683 | 11.3 | 1162.7757 | 11.3 | 1203.3185 | 11.3 | 1563.9294 | 11.3 | 1828.748 | 11.3
[10 empty] | 493.4945 | 11.4 | 646.0392 | 11.4 | 783.0242 | 11.4 | 1176.0901 | 11.4 | 1212.8448 | 11.4 | 1566.072 | 11.4 | 1842.0349 | 11.4
[10 empty] | 495.3099 | 11.5 | 651.5507 | 11.5 | 787.5801 | 11.5 | 1189.4045 | 11.5 | 1222.3712 | 11.5 | 1568.2146 | 11.5 | 1855.3219 | 11.5
[10 empty] | 497.1253 | 11.6 | 657.0622 | 11.6 | 792.1361 | 11.6 | 1202.7189 | 11.6 | 1231.8975 | 11.6 | 1570.3572 | 11.6 | 1868.6088 | 11.6
[10 empty] | 498.9406 | 11.7 | 662.5736 | 11.7 | 796.692 | 11.7 | 1216.0333 | 11.7 | 1241.4239 | 11.7 | 1572.4998 | 11.7 | 1881.8958 | 11.7
[10 empty] | 500.756 | 11.8 | 668.0851 | 11.8 | 801.2479 | 11.8 | 1229.3477 | 11.8 | 1250.9502 | 11.8 | 1574.6424 | 11.8 | 1895.1827 | 11.8
[10 empty] | 502.5713 | 11.9 | 673.5966 | 11.9 | 805.8038 | 11.9 | 1242.6621 | 11.9 | 1260.4766 | 11.9 | 1576.785 | 11.9 | 1908.4697 | 11.9
[10 empty] | 504.3867 | 12 | 679.1081 | 12 | 810.3598 | 12 | 1255.9765 | 12 | 1270.0029 | 12 | 1578.9277 | 12 | 1921.7566 | 12
[12 empty] | 684.6006 | 12.1 | 818.197 | 12.1 | 1267.2721 | 12.1 | 1283.2481 | 12.1 | 1580.2658 | 12.1 | 1941.1449 | 12.1
[12 empty] | 690.0932 | 12.2 | 826.0342 | 12.2 | 1278.5677 | 12.2 | 1296.4934 | 12.2 | 1581.604 | 12.2 | 1960.5332 | 12.2
[12 empty] | 695.5858 | 12.3 | 833.8714 | 12.3 | 1289.8632 | 12.3 | 1309.7386 | 12.3 | 1582.9422 | 12.3 | 1979.9216 | 12.3
[12 empty] | 701.0784 | 12.4 | 841.7086 | 12.4 | 1301.1588 | 12.4 | 1322.9838 | 12.4 | 1584.2804 | 12.4 | 1999.3099 | 12.4
[12 empty] | 706.571 | 12.5 | 849.5458 | 12.5 | 1312.4543 | 12.5 | 1336.229 | 12.5 | 1585.6186 | 12.5 | 2018.6982 | 12.5
[12 empty] | 712.0635 | 12.6 | 857.383 | 12.6 | 1323.7499 | 12.6 | 1349.4742 | 12.6 | 1586.9568 | 12.6 | 2038.0865 | 12.6
[12 empty] | 717.5561 | 12.7 | 865.2202 | 12.7 | 1335.0454 | 12.7 | 1362.7195 | 12.7 | 1588.295 | 12.7 | 2057.4749 | 12.7
[12 empty] | 723.0487 | 12.8 | 873.0574 | 12.8 | 1346.341 | 12.8 | 1375.9647 | 12.8 | 1589.6332 | 12.8 | 2076.8632 | 12.8
[12 empty] | 728.5413 | 12.9 | 880.8946 | 12.9 | 1357.6365 | 12.9 | 1389.2099 | 12.9 | 1590.9714 | 12.9 | 2096.2515 | 12.9
[12 empty] | 734.0338 | 13 | 888.7318 | 13 | 1368.9321 | 13 | 1402.4551 | 13 | 1592.3095 | 13 | 2115.6398 | 13
[12 empty] | 739.8721 | 13.1 | 897.2577 | 13.1 | 1376.847 | 13.1 | 1415.4352 | 13.1 | 1606.5187 | 13.1 | 2134.6828 | 13.1
[12 empty] | 745.7103 | 13.2 | 905.7836 | 13.2 | 1384.7619 | 13.2 | 1428.4153 | 13.2 | 1620.7279 | 13.2 | 2153.7257 | 13.2
[12 empty] | 751.5485 | 13.3 | 914.3095 | 13.3 | 1392.6768 | 13.3 | 1441.3954 | 13.3 | 1634.9371 | 13.3 | 2172.7686 | 13.3
[12 empty] | 757.3867 | 13.4 | 922.8354 | 13.4 | 1400.5917 | 13.4 | 1454.3755 | 13.4 | 1649.1463 | 13.4 | 2191.8116 | 13.4
[12 empty] | 763.2249 | 13.5 | 931.3613 | 13.5 | 1408.5066 | 13.5 | 1467.3556 | 13.5 | 1663.3555 | 13.5 | 2210.8545 | 13.5
[12 empty] | 769.0631 | 13.6 | 939.8872 | 13.6 | 1416.4215 | 13.6 | 1480.3357 | 13.6 | 1677.5647 | 13.6 | 2229.8975 | 13.6
[12 empty] | 774.9013 | 13.7 | 948.4131 | 13.7 | 1424.3363 | 13.7 | 1493.3158 | 13.7 | 1691.7739 | 13.7 | 2248.9404 | 13.7
[12 empty] | 780.7395 | 13.8 | 956.939 | 13.8 | 1432.2512 | 13.8 | 1506.2959 | 13.8 | 1705.9831 | 13.8 | 2267.9833 | 13.8
[12 empty] | 786.5777 | 13.9 | 965.4649 | 13.9 | 1440.1661 | 13.9 | 1519.276 | 13.9 | 1720.1923 | 13.9 | 2287.0263 | 13.9
[12 empty] | 792.4159 | 14 | 973.9908 | 14 | 1448.081 | 14 | 1532.2561 | 14 | 1734.4015 | 14 | 2306.0692 | 14
[12 empty] | 797.5109 | 14.1 | 981.0185 | 14.1 | 1460.338 | 14.1 | 1545.6621 | 14.1 | 1741.3878 | 14.1 | 2325.8085 | 14.1
[12 empty] | 802.606 | 14.2 | 988.0463 | 14.2 | 1472.595 | 14.2 | 1559.0682 | 14.2 | 1748.374 | 14.2 | 2345.5479 | 14.2
[12 empty] | 807.701 | 14.3 | 995.0741 | 14.3 | 1484.8521 | 14.3 | 1572.4742 | 14.3 | 1755.3602 | 14.3 | 2365.2872 | 14.3
[12 empty] | 812.7961 | 14.4 | 1002.1018 | 14.4 | 1497.1091 | 14.4 | 1585.8802 | 14.4 | 1762.3464 | 14.4 | 2385.0265 | 14.4
[12 empty] | 817.8912 | 14.5 | 1009.1296 | 14.5 | 1509.3661 | 14.5 | 1599.2863 | 14.5 | 1769.3327 | 14.5 | 2404.7659 | 14.5
[12 empty] | 822.9862 | 14.6 | 1016.1573 | 14.6 | 1521.6231 | 14.6 | 1612.6923 | 14.6 | 1776.3189 | 14.6 | 2424.5052 | 14.6
[12 empty] | 828.0813 | 14.7 | 1023.1851 | 14.7 | 1533.8801 | 14.7 | 1626.0983 | 14.7 | 1783.3051 | 14.7 | 2444.2445 | 14.7
[12 empty] | 833.1763 | 14.8 | 1030.2128 | 14.8 | 1546.1371 | 14.8 | 1639.5044 | 14.8 | 1790.2913 | 14.8 | 2463.9839 | 14.8
[12 empty] | 838.2714 | 14.9 | 1037.2406 | 14.9 | 1558.3941 | 14.9 | 1652.9104 | 14.9 | 1797.2776 | 14.9 | 2483.7232 | 14.9
[12 empty] | 843.3664 | 15 | 1044.2684 | 15 | 1570.6511 | 15 | 1666.3164 | 15 | 1804.2638 | 15 | 2503.4625 | 15
[12 empty] | 850.2026 | 15.1 | 1049.7194 | 15.1 | 1583.2076 | 15.1 | 1678.5452 | 15.1 | 1820.7239 | 15.1 | 2525.4659 | 15.1
[12 empty] | 857.0387 | 15.2 | 1055.1705 | 15.2 | 1595.764 | 15.2 | 1690.7739 | 15.2 | 1837.1841 | 15.2 | 2547.4694 | 15.2
[12 empty] | 863.8749 | 15.3 | 1060.6216 | 15.3 | 1608.3204 | 15.3 | 1703.0027 | 15.3 | 1853.6442 | 15.3 | 2569.4728 | 15.3
[12 empty] | 870.711 | 15.4 | 1066.0727 | 15.4 | 1620.8769 | 15.4 | 1715.2314 | 15.4 | 1870.1044 | 15.4 | 2591.4762 | 15.4
[12 empty] | 877.5472 | 15.5 | 1071.5238 | 15.5 | 1633.4333 | 15.5 | 1727.4602 | 15.5 | 1886.5645 | 15.5 | 2613.4796 | 15.5
[12 empty] | 884.3833 | 15.6 | 1076.9748 | 15.6 | 1645.9897 | 15.6 | 1739.689 | 15.6 | 1903.0246 | 15.6 | 2635.483 | 15.6
[12 empty] | 891.2195 | 15.7 | 1082.4259 | 15.7 | 1658.5462 | 15.7 | 1751.9177 | 15.7 | 1919.4848 | 15.7 | 2657.4864 | 15.7
[12 empty] | 898.0556 | 15.8 | 1087.877 | 15.8 | 1671.1026 | 15.8 | 1764.1465 | 15.8 | 1935.9449 | 15.8 | 2679.4899 | 15.8
[12 empty] | 904.8918 | 15.9 | 1093.3281 | 15.9 | 1683.659 | 15.9 | 1776.3752 | 15.9 | 1952.4051 | 15.9 | 2701.4933 | 15.9
[12 empty] | 911.728 | 16 | 1098.7792 | 16 | 1696.2155 | 16 | 1788.604 | 16 | 1968.8652 | 16 | 2723.4967 | 16
[16 empty] | 1709.8092 | 16.1 | 1803.3003 | 16.1 | 1985.9806 | 16.1 | 2743.528 | 16.1
[16 empty] | 1723.403 | 16.2 | 1817.9967 | 16.2 | 2003.096 | 16.2 | 2763.5593 | 16.2
[16 empty] | 1736.9967 | 16.3 | 1832.6931 | 16.3 | 2020.2114 | 16.3 | 2783.5907 | 16.3
[16 empty] | 1750.5905 | 16.4 | 1847.3894 | 16.4 | 2037.3268 | 16.4 | 2803.622 | 16.4
[16 empty] | 1764.1842 | 16.5 | 1862.0858 | 16.5 | 2054.4422 | 16.5 | 2823.6533 | 16.5
[16 empty] | 1777.778 | 16.6 | 1876.7822 | 16.6 | 2071.5576 | 16.6 | 2843.6847 | 16.6
[16 empty] | 1791.3717 | 16.7 | 1891.4785 | 16.7 | 2088.673 | 16.7 | 2863.716 | 16.7
[16 empty] | 1804.9655 | 16.8 | 1906.1749 | 16.8 | 2105.7884 | 16.8 | 2883.7473 | 16.8
[16 empty] | 1818.5593 | 16.9 | 1920.8712 | 16.9 | 2122.9038 | 16.9 | 2903.7786 | 16.9
[16 empty] | 1832.153 | 17 | 1935.5676 | 17 | 2140.0192 | 17 | 2923.81 | 17
[16 empty] | 1842.4906 | 17.1 | 1951.0868 | 17.1 | 2158.2217 | 17.1 | 2945.2512 | 17.1
[16 empty] | 1852.8283 | 17.2 | 1966.6061 | 17.2 | 2176.4243 | 17.2 | 2966.6924 | 17.2
[16 empty] | 1863.1659 | 17.3 | 1982.1253 | 17.3 | 2194.6268 | 17.3 | 2988.1336 | 17.3
[16 empty] | 1873.5035 | 17.4 | 1997.6446 | 17.4 | 2212.8294 | 17.4 | 3009.5748 | 17.4
[16 empty] | 1883.8411 | 17.5 | 2013.1638 | 17.5 | 2231.0319 | 17.5 | 3031.016 | 17.5
[16 empty] | 1894.1787 | 17.6 | 2028.6831 | 17.6 | 2249.2345 | 17.6 | 3052.4572 | 17.6
[16 empty] | 1904.5164 | 17.7 | 2044.2023 | 17.7 | 2267.4371 | 17.7 | 3073.8984 | 17.7
[16 empty] | 1914.854 | 17.8 | 2059.7216 | 17.8 | 2285.6396 | 17.8 | 3095.3396 | 17.8
[16 empty] | 1925.1916 | 17.9 | 2075.2408 | 17.9 | 2303.8422 | 17.9 | 3116.7809 | 17.9
[16 empty] | 1935.5292 | 18 | 2090.76 | 18 | 2322.0447 | 18 | 3138.2221 | 18
[16 empty] | 1950.4586 | 18.1 | 2100.5995 | 18.1 | 2342.4704 | 18.1 | 3162.5092 | 18.1
[16 empty] | 1965.388 | 18.2 | 2110.4389 | 18.2 | 2362.8961 | 18.2 | 3186.7963 | 18.2
[16 empty] | 1980.3174 | 18.3 | 2120.2783 | 18.3 | 2383.3218 | 18.3 | 3211.0834 | 18.3
[16 empty] | 1995.2468 | 18.4 | 2130.1177 | 18.4 | 2403.7474 | 18.4 | 3235.3706 | 18.4
[16 empty] | 2010.1762 | 18.5 | 2139.9571 | 18.5 | 2424.1731 | 18.5 | 3259.6577 | 18.5
[16 empty] | 2025.1056 | 18.6 | 2149.7965 | 18.6 | 2444.5988 | 18.6 | 3283.9448 | 18.6
[16 empty] | 2040.035 | 18.7 | 2159.6359 | 18.7 | 2465.0245 | 18.7 | 3308.2319 | 18.7
[16 empty] | 2054.9644 | 18.8 | 2169.4754 | 18.8 | 2485.4502 | 18.8 | 3332.519 | 18.8
[16 empty] | 2069.8939 | 18.9 | 2179.3148 | 18.9 | 2505.8759 | 18.9 | 3356.8062 | 18.9
[16 empty] | 2084.8233 | 19 | 2189.1542 | 19 | 2526.3015 | 19 | 3381.0933 | 19

## OPTIMA Compact Veriflow FCP
QUICK - CONTROL OPTIMA Compact Veriflow
Flow Commissioning program
Input
∆P measured = | 10 | kPa (PT plug in position Q)
Pre-set = | 2
Dimension | Range |  | Verification
| Flow (l/h) |  | Flow (l/h)
DN10 Low 2,5 | 30-200 |  | 87.5951
DN10 Low 5,0 | 65-370 |  | 137.8753
DN15 Low 2,5 | 30-200 |  | 87.5951
DN15 Low 5,0 | 65-370 |  | 137.8753
DN15 High 2,5 | 100-575 |  | 225.4704
DN15 High 5,0 | 220-1330 |  | 540.7495
DN20 High 2,5 | 100-575 |  | 225.4704
DN20 High 5,0 | 220-1330 |  | 540.7495
DN20 High 5,5 | 300-1800 |  | 635.6178
DN25 Low 5,5 | 280-1800 |  | 594.5082
DN25L High 5,5 | 600-3609 |  | 1268.0733
DN32 | 550-4001 |  | 1290.2093
DN40 | 1370-9500 |  | 3794.7332
DN50 | 1400-11500 |  | 3668.2421
Veriflow Low 2,5 DN10/15 |  | Veriflow Low 5,0 DN10/15 |  | Veriflow High 2,5 DN15/20 |  | Veriflow High 5,0 DN15/20 |  | Veriflow High 5,5 DN20 |  | Veriflow Low 5,5 DN25
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.5 | 0.121
0.6 | 0.124 | 0.6 | 0.134 | 0.6 | 0.25 | 0.6 | 0.595 | 0.6 | 0.675 | 0.6 | 0.647
0.8 | 0.136 | 0.8 | 0.184 | 0.8 | 0.314 | 0.8 | 0.755 | 0.8 | 0.849 | 0.8 | 0.77
1 | 0.153 | 1 | 0.231 | 1 | 0.378 | 1 | 0.913 | 1 | 1.03 | 1 | 0.916
1.2 | 0.174 | 1.2 | 0.275 | 1.2 | 0.442 | 1.2 | 1.07 | 1.2 | 1.22 | 1.2 | 1.08
1.4 | 0.198 | 1.4 | 0.317 | 1.4 | 0.507 | 1.4 | 1.23 | 1.4 | 1.41 | 1.4 | 1.26
1.6 | 0.224 | 1.6 | 0.357 | 1.6 | 0.574 | 1.6 | 1.39 | 1.6 | 1.61 | 1.6 | 1.46
1.8 | 0.25 | 1.8 | 0.397 | 1.8 | 0.642 | 1.8 | 1.55 | 1.8 | 1.81 | 1.8 | 1.66
2 | 0.277 | 2 | 0.436 | 2 | 0.713 | 2 | 1.71 | 2 | 2.01 | 2 | 1.88
2.2 | 0.303 | 2.2 | 0.475 | 2.2 | 0.786 | 2.2 | 1.88 | 2.2 | 2.21 | 2.2 | 2.09
2.4 | 0.328 | 2.4 | 0.515 | 2.4 | 0.86 | 2.4 | 2.04 | 2.4 | 2.41 | 2.4 | 2.31
2.6 | 0.352 | 2.6 | 0.555 | 2.6 | 0.936 | 2.6 | 2.21 | 2.6 | 2.61 | 2.6 | 2.52
2.8 | 0.375 | 2.8 | 0.595 | 2.8 | 1.01 | 2.8 | 2.38 | 2.8 | 2.8 | 2.8 | 2.73
3 | 0.397 | 3 | 0.636 | 3 | 1.09 | 3 | 2.55 | 3 | 2.99 | 3 | 2.93
3.2 | 0.418 | 3.2 | 0.677 | 3.2 | 1.17 | 3.2 | 2.72 | 3.2 | 3.17 | 3.2 | 3.13
3.4 | 0.439 | 3.4 | 0.718 | 3.4 | 1.24 | 3.4 | 2.88 | 3.4 | 3.34 | 3.4 | 3.32
3.6 | 0.46 | 3.6 | 0.76 | 3.6 | 1.31 | 3.6 | 3.03 | 3.6 | 3.51 | 3.6 | 3.49
3.8 | 0.482 | 3.8 | 0.8 | 3.8 | 1.38 | 3.8 | 3.18 | 3.8 | 3.66 | 3.8 | 3.65
4 | 0.506 | 4 | 0.839 | 4 | 1.44 | 4 | 3.31 | 4 | 3.8 | 4 | 3.8
Veriflow High 5,5 DN25L |  | Veriflow DN32 |  | Veriflow DN40 |  | Veriflow DN50
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.6 | 1.28 | 0.6 | 1.44 | 0.6 | 4.74 | 0.6 | 4.43
0.8 | 1.6847 | 0.8 | 1.8255 | 0.8 | 5.8162 | 0.8 | 5.3494
1 | 2.09 | 1 | 2.2 | 1 | 6.85 | 1 | 6.3
1.2 | 2.4913 | 1.2 | 2.5693 | 1.2 | 7.8621 | 1.2 | 7.2844
1.4 | 2.8855 | 1.4 | 2.9383 | 1.4 | 8.87 | 1.4 | 8.305
1.6 | 3.2704 | 1.6 | 3.311 | 1.6 | 9.8885 | 1.6 | 9.3636
1.8 | 3.6451 | 1.8 | 3.6908 | 1.8 | 10.929 | 1.8 | 10.4616
2 | 4.01 | 2 | 4.08 | 2 | 12 | 2 | 11.6
2.2 | 4.3665 | 2.2 | 4.4801 | 2.2 | 13.1071 | 2.2 | 12.7792
2.4 | 4.7173 | 2.4 | 4.8917 | 2.4 | 14.2528 | 2.4 | 13.9994
2.6 | 5.0663 | 2.6 | 5.3148 | 2.6 | 15.4364 | 2.6 | 15.2602
2.8 | 5.4184 | 2.8 | 5.7482 | 2.8 | 16.6543 | 2.8 | 16.5608
3 | 5.78 | 3 | 6.19 | 3 | 17.9 | 3 | 17.9
3.2 | 6.1584 | 3.2 | 6.6375 | 3.2 | 19.1638 | 3.2 | 18.74
3.4 | 6.5622 | 3.4 | 7.0872 | 3.4 | 20.4329 | 3.4 | 19.58
3.6 | 7.0012 | 3.6 | 7.5345 | 3.6 | 21.6916 | 3.6 | 20.42
3.8 | 7.4865 | 3.8 | 7.9742 | 3.8 | 22.9213 | 3.8 | 21.26
4 | 8.03 | 4 | 8.4 | 4 | 24.1 | 4 | 22.1

## OPTIMA Compact Veriflow fl FCP
QUICK - CONTROL OPTIMA Compact Veriflow Flanged
Flow Commissioning program
Input
∆P measured = | 15 | kPa (Use PT plugs P1 & P2)
Pre-set = | 4
Dimension | Range | Verification
| Flow (m3/h) | Flow (m3/h)
DN50 Ultra High Flow | 1.40-11.5 | 8.2882
DN50 Standard Low Flow | 2.50-15.0 | 15.337
DN50 Standard High Flow | 3.90-24.0 | 15.1434
DN65 Ultra Low Flow | 3.00-16.0 | 17.196
DN65 Ultra High Flow | 4.20-24.0 | 15.2208
DN65 Standard Low Flow | 4.40-25.0 | 20.9141
DN65 Standard High Flow | 6.00-35.0 | 21.0303
DN80 Ultra Low Flow | 4.40-25.0 | 20.9528
DN80 Ultra High Flow | 6.00-35.0 | 20.2557
DN80 Standard Low Flow | 5.30-34.0 | 29.1248
DN80 Standard High Flow | 7.00-43.0 | 29.2023
DN100 Ultra Low Flow | 5.30-34.0 | 30.7515
DN100 Ultra High Flow | 7.00-43.0 | 29.4347
DN100 Standard Low Flow | 12.1-68.0 | 65.0661
DN100 Standard High Flow | 14.8-90.0 | 68.9391
DN125 Ultra Low Flow | 12.1-68.0 | 58.482
DN125 Ultra High Flow | 14.8-90.0 | 69.3264
DN125 Standard Low Flow | 18.5-110 | 85.5929
DN125 Standard High Flow | 23.0-135 | 86.3675
DN150 Standard Low Flow | 25.6-148 | 104.9578
DN150 Standard High Flow | 32.0-195 | 107.2816
DN200 Standard Low Flow | 95.0-210 | 156.4685
DN200 Standard High Flow | 130-280 | 158.405
DN250 Standard Low Flow | 190-475 | 270.7215
DN250 Standard High Flow | 245-600 | 289.6992
DN300 Standard Low Flow | 190-475 | 269.9469
DN300 Standard High Flow | 245-600 | 288.9246
OPTIMA Veriflow Ultra DN50 HF |  | OPTIMA Veriflow Standard DN50 LF |  | OPTIMA Veriflow Standard DN50 HF |  | OPTIMA Veriflow Ultra DN65 LF |  | OPTIMA Veriflow Ultra DN65 HF |  | OPTIMA Veriflow Standard DN65 LF |  | OPTIMA Veriflow Standard DN65 HF
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.6 | 4.66 | 0.6 | 9.19 | 0.6 | 9.68 | 0.6 | 9.89 | 0.6 | 9.44 | 0.6 | 11.6 | 0.6 | 10.9
0.8 | 5.87 | 0.8 | 11.6904 | 0.8 | 11.9459 | 0.8 | 12.3 | 0.8 | 11.9 | 0.8 | 14.778 | 0.8 | 13.5956
1 | 7.11 | 1 | 13.9 | 1 | 14.1 | 1 | 14.4 | 1 | 14 | 1 | 17.5 | 1 | 16
1.2 | 8.34 | 1.2 | 15.8913 | 1.2 | 16.167 | 1.2 | 16.3 | 1.2 | 15.9 | 1.2 | 19.9096 | 1.2 | 18.2372
1.4 | 9.54 | 1.4 | 17.7274 | 1.4 | 18.167 | 1.4 | 18 | 1.4 | 17.7 | 1.4 | 22.1304 | 1.4 | 20.4114
1.6 | 10.7 | 1.6 | 19.4625 | 1.6 | 20.1158 | 1.6 | 19.7 | 1.6 | 19.5 | 1.6 | 24.2664 | 1.6 | 22.6068
1.8 | 11.7 | 1.8 | 21.1414 | 1.8 | 22.0245 | 1.8 | 21.5 | 1.8 | 21.2 | 1.8 | 26.4015 | 1.8 | 24.8881
2 | 12.7 | 2 | 22.8 | 2 | 23.9 | 2 | 23.4 | 2 | 22.9 | 2 | 28.6 | 2 | 27.3
2.2 | 13.6 | 2.2 | 24.4649 | 2.2 | 25.7444 | 2.2 | 25.4 | 2.2 | 24.7 | 2.2 | 30.9062 | 2.2 | 29.8675
2.4 | 14.4 | 2.4 | 26.1536 | 2.4 | 27.5556 | 2.4 | 27.5 | 2.4 | 26.5 | 2.4 | 33.3446 | 2.4 | 32.5957
2.6 | 15.1 | 2.6 | 27.8744 | 2.6 | 29.3268 | 2.6 | 29.8 | 2.6 | 28.3 | 2.6 | 35.9198 | 2.6 | 35.4701
2.8 | 15.8 | 2.8 | 29.6265 | 2.8 | 31.0468 | 2.8 | 32.2 | 2.8 | 30.1 | 2.8 | 38.6166 | 2.8 | 38.4563
3 | 16.5 | 3 | 31.4 | 3 | 32.7 | 3 | 34.6 | 3 | 32 | 3 | 41.4 | 3 | 41.5
3.2 | 17.2 | 3.2 | 33.1758 | 3.2 | 34.2661 | 3.2 | 37 | 3.2 | 33.8 | 3.2 | 44.2151 | 3.2 | 44.5273
3.4 | 18 | 3.4 | 34.9257 | 3.4 | 35.7206 | 3.4 | 39.3 | 3.4 | 35.5 | 3.4 | 46.9872 | 3.4 | 47.4444
3.6 | 18.9 | 3.6 | 36.6122 | 3.6 | 37.0342 | 3.6 | 41.4 | 3.6 | 37.1 | 3.6 | 49.6216 | 3.6 | 50.1378
3.8 | 20 | 3.8 | 38.1889 | 3.8 | 38.1734 | 3.8 | 43.1 | 3.8 | 38.3 | 3.8 | 52.004 | 3.8 | 52.474
4 | 21.4 | 4 | 39.6 | 4 | 39.1 | 4 | 44.4 | 4 | 39.3 | 4 | 54 | 4 | 54.3
OPTIMA Veriflow Ultra DN80 LF |  | OPTIMA Veriflow Ultra DN80 HF |  | OPTIMA Veriflow Standard DN80 LF |  | OPTIMA Veriflow Standard DN80 HF |  | OPTIMA Veriflow Ultra DN100 LF |  | OPTIMA Veriflow Ultra DN100 HF |  | OPTIMA Veriflow Standard DN100 LF |  | OPTIMA Veriflow Standard DN100 HF
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.6 | 10.4 | 0.6 | 10.8 | 0.6 | 14.9 | 0.6 | 15 | 0.6 | 15.6 | 0.6 | 16.8 | 0.6 | 35.2 | 0.6 | 35
0.8 | 12.8 | 0.8 | 13.2 | 0.8 | 18.7936 | 0.8 | 19.9303 | 0.8 | 19.2 | 0.8 | 19.9 | 0.8 | 43.3802 | 0.8 | 43.0131
1 | 15.2 | 1 | 15.5 | 1 | 22.4 | 1 | 24 | 1 | 22.6 | 1 | 23.1 | 1 | 50.2 | 1 | 49.6
1.2 | 17.5 | 1.2 | 17.9 | 1.2 | 25.8228 | 1.2 | 27.4924 | 1.2 | 26 | 1.2 | 26.3 | 1.2 | 56.0825 | 1.2 | 55.3489
1.4 | 19.9 | 1.4 | 20.2 | 1.4 | 29.1498 | 1.4 | 30.6493 | 1.4 | 29.4 | 1.4 | 29.7 | 1.4 | 61.4051 | 1.4 | 60.7644
1.6 | 22.2 | 1.6 | 22.7 | 1.6 | 32.4532 | 1.6 | 33.6708 | 1.6 | 33 | 1.6 | 33.1 | 1.6 | 66.4993 | 1.6 | 66.2673
1.8 | 24.5 | 1.8 | 25.1 | 1.8 | 35.7896 | 1.8 | 36.7154 | 1.8 | 36.6 | 1.8 | 36.7 | 1.8 | 71.6509 | 1.8 | 72.1947
2 | 26.9 | 2 | 27.6 | 2 | 39.2 | 2 | 39.9 | 2 | 40.5 | 2 | 40.5 | 2 | 77.1 | 2 | 78.8
2.2 | 29.3 | 2.2 | 30.1 | 2.2 | 42.7097 | 2.2 | 43.2998 | 2.2 | 44.5 | 2.2 | 44.4 | 2.2 | 83.0406 | 2.2 | 86.2528
2.4 | 31.7 | 2.4 | 32.7 | 2.4 | 46.3283 | 2.4 | 46.9485 | 2.4 | 48.7 | 2.4 | 48.4 | 2.4 | 89.6213 | 2.4 | 94.6389
2.6 | 34.2 | 2.6 | 35.2 | 2.6 | 50.0499 | 2.6 | 50.8381 | 2.6 | 53 | 2.6 | 52.4 | 2.6 | 96.9445 | 2.6 | 103.9605
2.8 | 36.8 | 2.8 | 37.8 | 2.8 | 53.8529 | 2.8 | 54.919 | 2.8 | 57.4 | 2.8 | 56.4 | 2.8 | 105.067 | 2.8 | 114.136
3 | 39.4 | 3 | 40.4 | 3 | 57.7 | 3 | 59.1 | 3 | 61.8 | 3 | 60.4 | 3 | 114 | 3 | 125
3.2 | 42.1 | 3.2 | 42.9 | 3.2 | 61.5384 | 3.2 | 63.2482 | 3.2 | 66.1 | 3.2 | 64.2 | 3.2 | 123.7085 | 3.2 | 136.3035
3.4 | 44.9 | 3.4 | 45.4 | 3.4 | 65.2996 | 3.4 | 67.1892 | 3.4 | 70.1 | 3.4 | 67.8 | 3.4 | 134.1121 | 3.4 | 147.7137
3.6 | 47.9 | 3.6 | 47.8 | 3.6 | 68.8994 | 3.6 | 70.7069 | 3.6 | 73.8 | 3.6 | 71.1 | 3.6 | 145.0843 | 3.6 | 158.814
3.8 | 50.9 | 3.8 | 50.1 | 3.8 | 72.238 | 3.8 | 73.5436 | 3.8 | 76.9 | 3.8 | 73.8 | 3.8 | 156.4529 | 3.8 | 169.1041
4 | 54.1 | 4 | 52.3 | 4 | 75.2 | 4 | 75.4 | 4 | 79.4 | 4 | 76 | 4 | 168 | 4 | 178
OPTIMA Veriflow Ultra DN125 LF |  | OPTIMA Veriflow Ultra DN125 HF |  | OPTIMA Veriflow Standard DN125 LF |  | OPTIMA Veriflow Standard DN125 HF
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
0.6 | 32.4 | 0.6 | 30.4 | 0.6 | 43.6 | 0.6 | 45.4
0.8 | 39.4 | 0.8 | 38.3 | 0.8 | 54.262 | 0.8 | 56.7184
1 | 45.7 | 1 | 45.9 | 1 | 64.4 | 1 | 67.4
1.2 | 51.4 | 1.2 | 53.2 | 1.2 | 74.2051 | 1.2 | 77.6724
1.4 | 56.9 | 1.4 | 60.2 | 1.4 | 83.8422 | 1.4 | 87.7282
1.6 | 62.2 | 1.6 | 67 | 1.6 | 93.4499 | 1.6 | 97.7252
1.8 | 67.7 | 1.8 | 73.7 | 1.8 | 103.1405 | 1.8 | 107.7864
2 | 73.4 | 2 | 80.4 | 2 | 113 | 2 | 118
2.2 | 79.4 | 2.2 | 87.2 | 2.2 | 123.0881 | 2.2 | 128.4193
2.4 | 85.9 | 2.4 | 94.2 | 2.4 | 133.4382 | 2.4 | 139.0627
2.6 | 92.8 | 2.6 | 102 | 2.6 | 144.0574 | 2.6 | 149.9139
2.8 | 100 | 2.8 | 109 | 2.8 | 154.9265 | 2.8 | 160.9217
3 | 108 | 3 | 118 | 3 | 166 | 3 | 172
3.2 | 116 | 3.2 | 127 | 3.2 | 177.2061 | 3.2 | 183.028
3.4 | 125 | 3.4 | 138 | 3.4 | 188.4467 | 3.4 | 193.85
3.6 | 134 | 3.6 | 150 | 3.6 | 199.5974 | 3.6 | 204.2754
3.8 | 142 | 3.8 | 164 | 3.8 | 210.5075 | 3.8 | 214.0788
4 | 151 | 4 | 179 | 4 | 221 | 4 | 223
OPTIMA Veriflow Standard DN150 LF |  | OPTIMA Veriflow Standard DN150 HF
Preset | KV signal | Preset | KV signal
0.6 | 60.8 | 0.6 | 59.8
0.8 | 77.0376 | 0.8 | 76.1074
1 | 92.3 | 1 | 91.6
1.2 | 106.7885 | 1.2 | 106.4142
1.4 | 120.6751 | 1.4 | 120.6689
1.6 | 134.1021 | 1.6 | 134.4654
1.8 | 147.1826 | 1.8 | 147.8871
2 | 160 | 2 | 161
2.2 | 172.6083 | 2.2 | 173.8522
2.4 | 185.0322 | 2.4 | 186.4743
2.6 | 197.2666 | 2.6 | 198.8791
2.8 | 209.2771 | 2.8 | 211.0618
3 | 221 | 3 | 223
3.2 | 232.3418 | 3.2 | 234.6535
3.4 | 243.1797 | 3.4 | 245.9646
3.6 | 253.3615 | 3.6 | 256.8577
3.8 | 262.7053 | 3.8 | 267.2398
4 | 271 | 4 | 277
OPTIMA Veriflow Standard DN200 LF |  | OPTIMA Veriflow Standard DN200 HF |  | OPTIMA Veriflow Standard DN250 LF |  | OPTIMA Veriflow Standard DN250 HF |  | OPTIMA Veriflow Standard DN300 LF |  | OPTIMA Veriflow Standard DN300 HF
Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal | Preset | KV signal
1 | 243 | 1 | 245 | 1 | 408 | 1 | 428 | 1 | 387 | 1 | 397
1.2 | 261.368 | 1.2 | 264.52 | 1.2 | 417.824 | 1.2 | 442 | 1.2 | 419.464 | 1.2 | 429.432
1.4 | 275.664 | 1.4 | 279.52 | 1.4 | 431.512 | 1.4 | 456 | 1.4 | 446.672 | 1.4 | 457.296
1.6 | 286.576 | 1.6 | 290.76 | 1.6 | 448.488 | 1.6 | 470 | 1.6 | 469.448 | 1.6 | 481.344
1.8 | 294.792 | 1.8 | 299 | 1.8 | 468.176 | 1.8 | 484 | 1.8 | 488.616 | 1.8 | 502.328
2 | 301 | 2 | 305 | 2 | 490 | 2 | 498 | 2 | 505 | 2 | 521
2.2 | 305.888 | 2.2 | 309.52 | 2.2 | 513.384 | 2.2 | 533.44 | 2.2 | 519.424 | 2.2 | 538.112
2.4 | 310.144 | 2.4 | 313.32 | 2.4 | 537.752 | 2.4 | 566.56 | 2.4 | 532.712 | 2.4 | 554.416
2.6 | 314.456 | 2.6 | 317.16 | 2.6 | 562.528 | 2.6 | 597.36 | 2.6 | 545.688 | 2.6 | 570.664
2.8 | 319.512 | 2.8 | 321.8 | 2.8 | 587.136 | 2.8 | 625.84 | 2.8 | 559.176 | 2.8 | 587.608
3 | 326 | 3 | 328 | 3 | 611 | 3 | 652 | 3 | 574 | 3 | 606
3.2 | 334.608 | 3.2 | 336.52 | 3.2 | 633.544 | 3.2 | 675.84 | 3.2 | 590.984 | 3.2 | 626.592
3.4 | 346.024 | 3.4 | 348.12 | 3.4 | 654.192 | 3.4 | 697.36 | 3.4 | 610.952 | 3.4 | 650.136
3.6 | 360.936 | 3.6 | 363.56 | 3.6 | 672.368 | 3.6 | 716.56 | 3.6 | 634.728 | 3.6 | 677.384
3.8 | 380.032 | 3.8 | 383.6 | 3.8 | 687.496 | 3.8 | 733.44 | 3.8 | 663.136 | 3.8 | 709.088
4 | 404 | 4 | 409 | 4 | 699 | 4 | 748 | 4 | 697 | 4 | 746
P1
P2
P3

## Frese STBV-VODRV FCP
QUICK - CONTROL Frese STBV, VODRV
Flow Commissioning program
Input
| ∆P measured = | 100 | (kPa) KV signal (For flow measurement)
| Pre-set = | 4
DN | KV signal (Fully open valve) |  | Verification Flow (l/h)
15 | 6.8 |  | 6800
20 | 9.9 |  | 9880
25 | 31.8 |  | 31790
32 | 23 |  | 23010
40 | 40 |  | 39950
50 | 49.7 |  | 42700
| DN 15 |  | DN20 |  | DN25 |  | DN32 |  | DN40 |  | DN50
Einstellung | KV signal | KV total | KV signal | KV total | KV signal | KV total | KV signal | KV total | Einstellung | KV signal | KV signal | KV total
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.1 | 0.2 | 0.19 | 0.328 | 0.316 | 0.548 | 0.5 | 0.726 | 0.72 | 0.576 | 0.568 | 1.088 | 1.112
0.2 | 0.4 | 0.38 | 0.656 | 0.632 | 1.096 | 1 | 1.452 | 1.44 | 1.152 | 1.136 | 2.176 | 2.224
0.3 | 0.6 | 0.57 | 0.984 | 0.948 | 1.644 | 1.5 | 2.178 | 2.16 | 1.728 | 1.704 | 3.264 | 3.336
0.4 | 0.8 | 0.76 | 1.312 | 1.264 | 2.192 | 2 | 2.904 | 2.88 | 2.304 | 2.272 | 4.352 | 4.448
0.5 | 1 | 0.95 | 1.64 | 1.58 | 2.74 | 2.5 | 3.63 | 3.6 | 2.88 | 2.84 | 5.44 | 5.56
0.6 | 1.124 | 1.058 | 1.884 | 1.786 | 3.4026 | 2.914 | 4.358 | 4.312 | 3.972 | 3.936 | 6.75 | 6.916
0.7 | 1.248 | 1.166 | 2.128 | 1.992 | 4.0652 | 3.328 | 5.086 | 5.024 | 5.064 | 5.032 | 8.06 | 8.272
0.8 | 1.372 | 1.274 | 2.372 | 2.198 | 4.7278 | 3.742 | 5.814 | 5.736 | 6.156 | 6.128 | 9.37 | 9.628
0.9 | 1.496 | 1.382 | 2.616 | 2.404 | 5.3904 | 4.156 | 6.542 | 6.448 | 7.248 | 7.224 | 10.68 | 10.984
1 | 1.62 | 1.49 | 2.86 | 2.61 | 6.053 | 4.57 | 7.27 | 7.16 | 8.34 | 8.32 | 11.99 | 12.34
1.1 | 1.724 | 1.572 | 3.05 | 2.784 | 7.0844 | 4.946 | 8.018 | 7.822 | 9.496 | 9.276 | 13.122 | 13.39
1.2 | 1.828 | 1.654 | 3.24 | 2.958 | 8.1158 | 5.322 | 8.766 | 8.484 | 10.652 | 10.232 | 14.254 | 14.44
1.3 | 1.932 | 1.736 | 3.43 | 3.132 | 9.1472 | 5.698 | 9.514 | 9.146 | 11.808 | 11.188 | 15.386 | 15.49
1.4 | 2.036 | 1.818 | 3.62 | 3.306 | 10.1786 | 6.074 | 10.262 | 9.808 | 12.964 | 12.144 | 16.518 | 16.54
1.5 | 2.14 | 1.9 | 3.81 | 3.48 | 11.21 | 6.45 | 11.01 | 10.47 | 14.12 | 13.1 | 17.65 | 17.59
1.6 | 2.242 | 1.974 | 4.002 | 3.622 | 12.142 | 6.682 | 11.54 | 10.968 | 15.03 | 13.736 | 18.668 | 18.498
1.7 | 2.344 | 2.048 | 4.194 | 3.764 | 13.074 | 6.914 | 12.07 | 11.466 | 15.94 | 14.372 | 19.686 | 19.406
1.8 | 2.446 | 2.122 | 4.386 | 3.906 | 14.006 | 7.146 | 12.6 | 11.964 | 16.85 | 15.008 | 20.704 | 20.314
1.9 | 2.548 | 2.196 | 4.578 | 4.048 | 14.938 | 7.378 | 13.13 | 12.462 | 17.76 | 15.644 | 21.722 | 21.222
2 | 2.65 | 2.27 | 4.77 | 4.19 | 15.87 | 7.61 | 13.66 | 12.96 | 18.67 | 16.28 | 22.74 | 22.13
2.1 | 2.698 | 2.316 | 4.92 | 4.324 | 16.838 | 7.828 | 14.132 | 13.416 | 19.542 | 16.87 | 23.766 | 22.834
2.2 | 2.746 | 2.362 | 5.07 | 4.458 | 17.806 | 8.046 | 14.604 | 13.872 | 20.414 | 17.46 | 24.792 | 23.538
2.3 | 2.794 | 2.408 | 5.22 | 4.592 | 18.774 | 8.264 | 15.076 | 14.328 | 21.286 | 18.05 | 25.818 | 24.242
2.4 | 2.842 | 2.454 | 5.37 | 4.726 | 19.742 | 8.482 | 15.548 | 14.784 | 22.158 | 18.64 | 26.844 | 24.946
2.5 | 2.89 | 2.5 | 5.52 | 4.86 | 20.71 | 8.7 | 16.02 | 15.24 | 23.03 | 19.23 | 27.87 | 25.65
2.6 | 3.116 | 2.578 | 5.716 | 4.986 | 21.566 | 8.84 | 16.458 | 15.646 | 23.812 | 19.722 | 28.76 | 26.412
2.7 | 3.342 | 2.656 | 5.912 | 5.112 | 22.422 | 8.98 | 16.896 | 16.052 | 24.594 | 20.214 | 29.65 | 27.174
2.8 | 3.568 | 2.734 | 6.108 | 5.238 | 23.278 | 9.12 | 17.334 | 16.458 | 25.376 | 20.706 | 30.54 | 27.936
2.9 | 3.794 | 2.812 | 6.304 | 5.364 | 24.134 | 9.26 | 17.772 | 16.864 | 26.158 | 21.198 | 31.43 | 28.698
3 | 4.02 | 2.89 | 6.5 | 5.49 | 24.99 | 9.4 | 18.21 | 17.27 | 26.94 | 21.69 | 32.32 | 29.46
3.1 | 4.288 | 2.952 | 6.772 | 5.61 | 26.194 | 9.544 | 18.718 | 17.682 | 28.148 | 22.166 | 33.332 | 30.194
3.2 | 4.556 | 3.014 | 7.044 | 5.73 | 27.398 | 9.688 | 19.226 | 18.094 | 29.356 | 22.642 | 34.344 | 30.928
3.3 | 4.824 | 3.076 | 7.316 | 5.85 | 28.602 | 9.832 | 19.734 | 18.506 | 30.564 | 23.118 | 35.356 | 31.662
3.4 | 5.092 | 3.138 | 7.588 | 5.97 | 29.806 | 9.976 | 20.242 | 18.918 | 31.772 | 23.594 | 36.368 | 32.396
3.5 | 5.36 | 3.2 | 7.86 | 6.09 | 31.01 | 10.12 | 20.75 | 19.33 | 32.98 | 24.07 | 37.38 | 33.13
3.6 | 5.648 | 3.258 | 8.264 | 6.172 | 31.166 | 10.196 | 21.202 | 19.664 | 34.374 | 24.456 | 38.444 | 33.768
3.7 | 5.936 | 3.316 | 8.668 | 6.254 | 31.322 | 10.272 | 21.654 | 19.998 | 35.768 | 24.842 | 39.508 | 34.406
3.8 | 6.224 | 3.374 | 9.072 | 6.336 | 31.478 | 10.348 | 22.106 | 20.332 | 37.162 | 25.228 | 40.572 | 35.044
3.9 | 6.512 | 3.432 | 9.476 | 6.418 | 31.634 | 10.424 | 22.558 | 20.666 | 38.556 | 25.614 | 41.636 | 35.682
4 | 6.8 | 3.49 | 9.88 | 6.5 | 31.79 | 10.5 | 23.01 | 21 | 39.95 | 26 | 42.7 | 36.32
4.1 | [10 empty] | 44.1 | 37.056
4.2 | [10 empty] | 45.5 | 37.792
4.3 | [10 empty] | 46.9 | 38.528
4.4 | [10 empty] | 48.3 | 39.264
4.5 | [10 empty] | 49.7 | 40

## Frese STBV-VODRV flanged FCP
QUICK - CONTROL Frese STBV, VODRV Flanged
Flow Commissioning program
Input
| ∆P measured = | 10 | (kPa) Total valve
| Pre-set = | 8
DN | KV (Fully open valve) |  | Verification Flow (m3/h)
65 | 64.1139 |  | 20.2746
80 | 85.4081 |  | 27.0084
100 | 119.2742 |  | 37.7178
125 | 202.5046 |  | 64.0376
150 | 263.1266 |  | 83.2079
200 | 504.3867 |  | 115.2834
250 | 911.728 |  | 155.9824
300 | 1098.7792 |  | 202.4261
350 | 2084.8233 |  | 301.6536
400 | 2189.1542 |  | 341.4656
450 | 2526.3015 |  | 404.343
500 | 3381.0933 |  | 508.831
| DN65 | DN80 | DN100 | DN125 | DN150 | DN200 | DN250 | DN300 | DN350 | DN400 | DN450 | DN500
Einstellung | KV | KV | KV | KV | KV | KV | KV | KV | KV | KV | KV | KV
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.1 | 1.6813 | 1.6827 | 2.5113 | 3.9673 | 7.7206 | 13.4068 | 10.4302 | 12.9601 | 16.8991 | 23.2404 | 25.4536 | 32.1578
0.2 | 3.3625 | 3.3654 | 5.0226 | 7.9347 | 15.4411 | 26.8137 | 20.8604 | 25.9202 | 33.7981 | 46.4808 | 50.9073 | 64.3155
0.3 | 5.0438 | 5.0481 | 7.5339 | 11.902 | 23.1617 | 40.2205 | 31.2906 | 38.8804 | 50.6972 | 69.7212 | 76.3609 | 96.4733
0.4 | 6.7251 | 6.7308 | 10.0452 | 15.8694 | 30.8823 | 53.6273 | 41.7208 | 51.8405 | 67.5963 | 92.9616 | 101.8145 | 128.6311
0.5 | 8.4064 | 8.4136 | 12.5565 | 19.8367 | 38.6028 | 67.0341 | 52.151 | 64.8006 | 84.4954 | 116.202 | 127.2681 | 160.7888
0.6 | 10.0876 | 10.0963 | 15.0678 | 23.804 | 46.3234 | 80.441 | 62.5811 | 77.7607 | 101.3944 | 139.4424 | 152.7218 | 192.9466
0.7 | 11.7689 | 11.779 | 17.579 | 27.7714 | 54.044 | 93.8478 | 73.0113 | 90.7209 | 118.2935 | 162.6828 | 178.1754 | 225.1044
0.8 | 13.4502 | 13.4617 | 20.0903 | 31.7387 | 61.7645 | 107.2546 | 83.4415 | 103.681 | 135.1926 | 185.9232 | 203.629 | 257.2621
0.9 | 15.1314 | 15.1444 | 22.6016 | 35.7061 | 69.4851 | 120.6615 | 93.8717 | 116.6411 | 152.0916 | 209.1636 | 229.0826 | 289.4199
1 | 16.8127 | 16.8271 | 25.1129 | 39.6734 | 77.2057 | 134.0683 | 104.3019 | 129.6012 | 168.9907 | 232.404 | 254.5363 | 321.5777
1.1 | 17.6505 | 18.3266 | 26.9914 | 42.4793 | 81.1196 | 138.8057 | 109.4093 | 138.3336 | 181.8949 | 247.5387 | 269.2989 | 345.9495
1.2 | 18.4883 | 19.826 | 28.8698 | 45.2852 | 85.0335 | 143.5432 | 114.5168 | 147.066 | 194.7992 | 262.6734 | 284.0616 | 370.3214
1.3 | 19.3261 | 21.3255 | 30.7483 | 48.0911 | 88.9475 | 148.2806 | 119.6242 | 155.7983 | 207.7034 | 277.8082 | 298.8242 | 394.6933
1.4 | 20.1639 | 22.8249 | 32.6267 | 50.897 | 92.8614 | 153.018 | 124.7316 | 164.5307 | 220.6076 | 292.9429 | 313.5869 | 419.0652
1.5 | 21.0017 | 24.3244 | 34.5052 | 53.7029 | 96.7753 | 157.7555 | 129.839 | 173.2631 | 233.5119 | 308.0776 | 328.3495 | 443.437
1.6 | 21.8396 | 25.8238 | 36.3836 | 56.5088 | 100.6893 | 162.4929 | 134.9465 | 181.9954 | 246.4161 | 323.2123 | 343.1122 | 467.8089
1.7 | 22.6774 | 27.3233 | 38.2621 | 59.3147 | 104.6032 | 167.2303 | 140.0539 | 190.7278 | 259.3203 | 338.347 | 357.8749 | 492.1808
1.8 | 23.5152 | 28.8227 | 40.1405 | 62.1206 | 108.5172 | 171.9678 | 145.1613 | 199.4602 | 272.2246 | 353.4817 | 372.6375 | 516.5527
1.9 | 24.353 | 30.3222 | 42.019 | 64.9265 | 112.4311 | 176.7052 | 150.2687 | 208.1925 | 285.1288 | 368.6165 | 387.4002 | 540.9245
2 | 25.1908 | 31.8216 | 43.8975 | 67.7324 | 116.345 | 181.4426 | 155.3762 | 216.9249 | 298.033 | 383.7512 | 402.1628 | 565.2964
2.1 | 25.9802 | 32.6971 | 45.4598 | 70.2834 | 119.4408 | 185.226 | 163.0773 | 224.7888 | 311.5089 | 398.0993 | 418.4651 | 587.152
2.2 | 26.7697 | 33.5726 | 47.0221 | 72.8344 | 122.5367 | 189.0094 | 170.7785 | 232.6527 | 324.9848 | 412.4474 | 434.7673 | 609.0076
2.3 | 27.5592 | 34.448 | 48.5844 | 75.3854 | 125.6325 | 192.7928 | 178.4796 | 240.5166 | 338.4607 | 426.7956 | 451.0696 | 630.8633
2.4 | 28.3486 | 35.3235 | 50.1468 | 77.9364 | 128.7283 | 196.5762 | 186.1807 | 248.3805 | 351.9366 | 441.1437 | 467.3719 | 652.7189
2.5 | 29.1381 | 36.199 | 51.7091 | 80.4874 | 131.8241 | 200.3597 | 193.8819 | 256.2444 | 365.4125 | 455.4918 | 483.6741 | 674.5745
2.6 | 29.9276 | 37.0744 | 53.2714 | 83.0384 | 134.9199 | 204.1431 | 201.583 | 264.1083 | 378.8884 | 469.8399 | 499.9764 | 696.4301
2.7 | 30.717 | 37.9499 | 54.8338 | 85.5894 | 138.0157 | 207.9265 | 209.2842 | 271.9722 | 392.3643 | 484.1881 | 516.2786 | 718.2858
2.8 | 31.5065 | 38.8254 | 56.3961 | 88.1404 | 141.1116 | 211.7099 | 216.9853 | 279.8361 | 405.8402 | 498.5362 | 532.5809 | 740.1414
2.9 | 32.296 | 39.7008 | 57.9584 | 90.6914 | 144.2074 | 215.4933 | 224.6864 | 287.7 | 419.3161 | 512.8843 | 548.8832 | 761.997
3 | 33.0854 | 40.5763 | 59.5207 | 93.2424 | 147.3032 | 219.2767 | 232.3876 | 295.5638 | 432.792 | 527.2324 | 565.1854 | 783.8526
3.1 | 33.5191 | 41.3068 | 60.971 | 95.3369 | 150.3589 | 221.4227 | 238.2836 | 302.9298 | 444.7623 | 541.2176 | 581.867 | 804.5787
3.2 | 33.9528 | 42.0372 | 62.4213 | 97.4314 | 153.4146 | 223.5686 | 244.1796 | 310.2958 | 456.7326 | 555.2027 | 598.5486 | 825.3048
3.3 | 34.3866 | 42.7676 | 63.8716 | 99.5259 | 156.4702 | 225.7146 | 250.0756 | 317.6618 | 468.7028 | 569.1879 | 615.2301 | 846.0308
3.4 | 34.8203 | 43.4981 | 65.3219 | 101.6204 | 159.5259 | 227.8606 | 255.9717 | 325.0278 | 480.6731 | 583.173 | 631.9117 | 866.7569
3.5 | 35.254 | 44.2285 | 66.7722 | 103.715 | 162.5816 | 230.0066 | 261.8677 | 332.3938 | 492.6434 | 597.1582 | 648.5933 | 887.483
3.6 | 35.6877 | 44.959 | 68.2224 | 105.8095 | 165.6373 | 232.1526 | 267.7637 | 339.7598 | 504.6136 | 611.1433 | 665.2748 | 908.209
3.7 | 36.1214 | 45.6894 | 69.6727 | 107.904 | 168.693 | 234.2985 | 273.6597 | 347.1258 | 516.5839 | 625.1285 | 681.9564 | 928.9351
3.8 | 36.5551 | 46.4199 | 71.123 | 109.9985 | 171.7487 | 236.4445 | 279.5557 | 354.4918 | 528.5542 | 639.1136 | 698.638 | 949.6612
3.9 | 36.9888 | 47.1503 | 72.5733 | 112.093 | 174.8044 | 238.5905 | 285.4518 | 361.8578 | 540.5244 | 653.0987 | 715.3195 | 970.3872
4 | 37.4225 | 47.8808 | 74.0236 | 114.1875 | 177.8601 | 240.7365 | 291.3478 | 369.2238 | 552.4947 | 667.0839 | 732.0011 | 991.1133
4.1 | 37.8955 | 48.7487 | 75.0305 | 115.8509 | 180.529 | 242.7062 | 297.2556 | 375.3299 | 565.0749 | 680.1528 | 746.04 | 1010.831
4.2 | 38.3686 | 49.6167 | 76.0375 | 117.5143 | 183.1979 | 244.6758 | 303.1635 | 381.4359 | 577.655 | 693.2217 | 760.0789 | 1030.5486
4.3 | 38.8416 | 50.4847 | 77.0444 | 119.1777 | 185.8668 | 246.6455 | 309.0713 | 387.5419 | 590.2351 | 706.2906 | 774.1178 | 1050.2663
4.4 | 39.3146 | 51.3527 | 78.0513 | 120.8411 | 188.5357 | 248.6152 | 314.9792 | 393.6479 | 602.8153 | 719.3594 | 788.1568 | 1069.9839
4.5 | 39.7876 | 52.2207 | 79.0583 | 122.5046 | 191.2047 | 250.5849 | 320.887 | 399.7539 | 615.3954 | 732.4283 | 802.1957 | 1089.7016
4.6 | 40.2607 | 53.0887 | 80.0652 | 124.168 | 193.8736 | 252.5546 | 326.7948 | 405.86 | 627.9756 | 745.4972 | 816.2346 | 1109.4193
4.7 | 40.7337 | 53.9567 | 81.0722 | 125.8314 | 196.5425 | 254.5243 | 332.7027 | 411.966 | 640.5557 | 758.5661 | 830.2735 | 1129.1369
4.8 | 41.2067 | 54.8247 | 82.0791 | 127.4948 | 199.2114 | 256.4939 | 338.6105 | 418.072 | 653.1359 | 771.635 | 844.3124 | 1148.8546
4.9 | 41.6798 | 55.6926 | 83.0861 | 129.1582 | 201.8804 | 258.4636 | 344.5184 | 424.178 | 665.716 | 784.7039 | 858.3513 | 1168.5723
5 | 42.1528 | 56.5606 | 84.093 | 130.8216 | 204.5493 | 260.4333 | 350.4262 | 430.2841 | 678.2962 | 797.7728 | 872.3902 | 1188.2899
5.1 | 42.9191 | 57.5061 | 85.2349 | 133.3249 | 206.9476 | 263.4643 | 356.5787 | 436.8331 | 688.2255 | 808.4162 | 887.4938 | 1206.1978
5.2 | 43.6855 | 58.4515 | 86.3768 | 135.8282 | 209.346 | 266.4952 | 362.7311 | 443.3821 | 698.1548 | 819.0596 | 902.5975 | 1224.1056
5.3 | 44.4518 | 59.3969 | 87.5187 | 138.3315 | 211.7443 | 269.5262 | 368.8836 | 449.9311 | 708.0841 | 829.703 | 917.7011 | 1242.0135
5.4 | 45.2182 | 60.3423 | 88.6606 | 140.8349 | 214.1427 | 272.5572 | 375.036 | 456.4801 | 718.0134 | 840.3464 | 932.8047 | 1259.9213
5.5 | 45.9845 | 61.2877 | 89.8024 | 143.3382 | 216.541 | 275.5881 | 381.1885 | 463.0291 | 727.9427 | 850.9898 | 947.9083 | 1277.8292
5.6 | 46.7509 | 62.2332 | 90.9443 | 145.8415 | 218.9394 | 278.6191 | 387.341 | 469.5781 | 737.872 | 861.6332 | 963.012 | 1295.737
5.7 | 47.5172 | 63.1786 | 92.0862 | 148.3448 | 221.3377 | 281.65 | 393.4934 | 476.1271 | 747.8013 | 872.2766 | 978.1156 | 1313.6448
5.8 | 48.2836 | 64.124 | 93.2281 | 150.8481 | 223.7361 | 284.681 | 399.6459 | 482.6761 | 757.7306 | 882.92 | 993.2192 | 1331.5527
5.9 | 49.0499 | 65.0694 | 94.37 | 153.3514 | 226.1344 | 287.712 | 405.7983 | 489.2251 | 767.6599 | 893.5633 | 1008.3228 | 1349.4605
6 | 49.8162 | 66.0148 | 95.5119 | 155.8547 | 228.5327 | 290.7429 | 411.9508 | 495.7742 | 777.5892 | 904.2067 | 1023.4265 | 1367.3684
6.1 | 50.6566 | 67.0073 | 96.7313 | 158.321 | 230.5761 | 294.182 | 417.0726 | 503.3833 | 786.8066 | 913.4261 | 1035.2657 | 1380.8412
6.2 | 51.4969 | 67.9997 | 97.9507 | 160.7873 | 232.6195 | 297.621 | 422.1944 | 510.9924 | 796.024 | 922.6455 | 1047.105 | 1394.314
6.3 | 52.3373 | 68.9922 | 99.1702 | 163.2536 | 234.6629 | 301.06 | 427.3163 | 518.6015 | 805.2414 | 931.8648 | 1058.9443 | 1407.7869
6.4 | 53.1776 | 69.9846 | 100.3896 | 165.7199 | 236.7062 | 304.4991 | 432.4381 | 526.2106 | 814.4588 | 941.0842 | 1070.7836 | 1421.2597
6.5 | 54.0179 | 70.977 | 101.6091 | 168.1862 | 238.7496 | 307.9381 | 437.5599 | 533.8197 | 823.6762 | 950.3036 | 1082.6229 | 1434.7325
6.6 | 54.8583 | 71.9695 | 102.8285 | 170.6525 | 240.793 | 311.3771 | 442.6817 | 541.4288 | 832.8936 | 959.5229 | 1094.4622 | 1448.2053
6.7 | 55.6986 | 72.9619 | 104.048 | 173.1188 | 242.8364 | 314.8161 | 447.8036 | 549.0379 | 842.111 | 968.7423 | 1106.3014 | 1461.6781
6.8 | 56.5389 | 73.9544 | 105.2674 | 175.5851 | 244.8797 | 318.2552 | 452.9254 | 556.647 | 851.3284 | 977.9616 | 1118.1407 | 1475.151
6.9 | 57.3793 | 74.9468 | 106.4868 | 178.0514 | 246.9231 | 321.6942 | 458.0472 | 564.2561 | 860.5458 | 987.181 | 1129.98 | 1488.6238
7 | 58.2196 | 75.9392 | 107.7063 | 180.5177 | 248.9665 | 325.1332 | 463.169 | 571.8652 | 869.7632 | 996.4004 | 1141.8193 | 1502.0966
7.1 | 58.809 | 76.8861 | 108.8631 | 182.7164 | 250.3825 | 329.0757 | 466.1781 | 578.6914 | 878.1781 | 1004.7412 | 1155.5018 | 1512.7934
7.2 | 59.3985 | 77.833 | 110.0199 | 184.9151 | 251.7985 | 333.0182 | 469.1871 | 585.5177 | 886.5931 | 1013.0821 | 1169.1844 | 1523.4903
7.3 | 59.9879 | 78.7799 | 111.1767 | 187.1138 | 253.2145 | 336.9606 | 472.1962 | 592.3439 | 895.008 | 1021.423 | 1182.8669 | 1534.1871
7.4 | 60.5773 | 79.7268 | 112.3334 | 189.3125 | 254.6305 | 340.9031 | 475.2053 | 599.1701 | 903.4229 | 1029.7639 | 1196.5495 | 1544.8839
7.5 | 61.1667 | 80.6737 | 113.4902 | 191.5111 | 256.0465 | 344.8456 | 478.2143 | 605.9963 | 911.8379 | 1038.1047 | 1210.2321 | 1555.5807
7.6 | 61.7562 | 81.6206 | 114.647 | 193.7098 | 257.4625 | 348.7881 | 481.2234 | 612.8226 | 920.2528 | 1046.4456 | 1223.9146 | 1566.2776
7.7 | 62.3456 | 82.5674 | 115.8038 | 195.9085 | 258.8785 | 352.7305 | 484.2324 | 619.6488 | 928.6678 | 1054.7865 | 1237.5972 | 1576.9744
7.8 | 62.935 | 83.5143 | 116.9606 | 198.1072 | 260.2946 | 356.673 | 487.2415 | 626.475 | 937.0827 | 1063.1274 | 1251.2797 | 1587.6712
7.9 | 63.5245 | 84.4612 | 118.1174 | 200.3059 | 261.7106 | 360.6155 | 490.2505 | 633.3012 | 945.4976 | 1071.4682 | 1264.9623 | 1598.368
8 | 64.1139 | 85.4081 | 119.2742 | 202.5046 | 263.1266 | 364.558 | 493.2596 | 640.1274 | 953.9126 | 1079.8091 | 1278.6448 | 1609.0649
8.1 | [5 empty] | 368.5717 | 497.0464 | 646.6795 | 959.0791 | 1083.8874 | 1284.3629 | 1618.2765
8.2 | [5 empty] | 372.5854 | 500.8332 | 653.2316 | 964.2455 | 1087.9657 | 1290.081 | 1627.4881
8.3 | [5 empty] | 376.5992 | 504.62 | 659.7837 | 969.412 | 1092.044 | 1295.7991 | 1636.6997
8.4 | [5 empty] | 380.6129 | 508.4068 | 666.3357 | 974.5785 | 1096.1223 | 1301.5172 | 1645.9113
8.5 | [5 empty] | 384.6267 | 512.1936 | 672.8878 | 979.7449 | 1100.2006 | 1307.2353 | 1655.1229
8.6 | [5 empty] | 388.6404 | 515.9804 | 679.4399 | 984.9114 | 1104.2789 | 1312.9533 | 1664.3345
8.7 | [5 empty] | 392.6541 | 519.7672 | 685.992 | 990.0779 | 1108.3572 | 1318.6714 | 1673.5461
8.8 | [5 empty] | 396.6679 | 523.554 | 692.544 | 995.2444 | 1112.4355 | 1324.3895 | 1682.7577
8.9 | [5 empty] | 400.6816 | 527.3408 | 699.0961 | 1000.4108 | 1116.5138 | 1330.1076 | 1691.9693
9 | [5 empty] | 404.6953 | 531.1276 | 705.6482 | 1005.5773 | 1120.5921 | 1335.8257 | 1701.1809
9.1 | [5 empty] | 409.1841 | 536.3135 | 710.0286 | 1007.8488 | 1122.9188 | 1346.502 | 1706.3701
9.2 | [5 empty] | 413.673 | 541.4994 | 714.409 | 1010.1202 | 1125.2455 | 1357.1783 | 1711.5593
9.3 | [5 empty] | 418.1618 | 546.6853 | 718.7894 | 1012.3917 | 1127.5722 | 1367.8546 | 1716.7485
9.4 | [5 empty] | 422.6506 | 551.8712 | 723.1698 | 1014.6631 | 1129.8989 | 1378.531 | 1721.9377
9.5 | [5 empty] | 427.1394 | 557.0571 | 727.5503 | 1016.9346 | 1132.2256 | 1389.2073 | 1727.1269
9.6 | [5 empty] | 431.6282 | 562.243 | 731.9307 | 1019.206 | 1134.5523 | 1399.8836 | 1732.3161
9.7 | [5 empty] | 436.117 | 567.4289 | 736.3111 | 1021.4775 | 1136.879 | 1410.5599 | 1737.5053
9.8 | [5 empty] | 440.6058 | 572.6148 | 740.6915 | 1023.7489 | 1139.2057 | 1421.2363 | 1742.6945
9.9 | [5 empty] | 445.0946 | 577.8007 | 745.0719 | 1026.0204 | 1141.5324 | 1431.9126 | 1747.8837
10 | [5 empty] | 449.5835 | 582.9866 | 749.4523 | 1028.2918 | 1143.8591 | 1442.5889 | 1753.0729
10.1 | [5 empty] | 453.2484 | 587.0872 | 750.9872 | 1037.7459 | 1146.9471 | 1454.0802 | 1756.6543
10.2 | [5 empty] | 456.9134 | 591.1879 | 752.522 | 1047.2 | 1150.0352 | 1465.5714 | 1760.2358
10.3 | [5 empty] | 460.5783 | 595.2886 | 754.0568 | 1056.654 | 1153.1232 | 1477.0627 | 1763.8172
10.4 | [5 empty] | 464.2433 | 599.3893 | 755.5916 | 1066.1081 | 1156.2113 | 1488.554 | 1767.3986
10.5 | [5 empty] | 467.9083 | 603.4899 | 757.1264 | 1075.5622 | 1159.2993 | 1500.0452 | 1770.98
10.6 | [5 empty] | 471.5732 | 607.5906 | 758.6612 | 1085.0162 | 1162.3873 | 1511.5365 | 1774.5615
10.7 | [5 empty] | 475.2382 | 611.6913 | 760.1961 | 1094.4703 | 1165.4754 | 1523.0277 | 1778.1429
10.8 | [5 empty] | 478.9032 | 615.7919 | 761.7309 | 1103.9243 | 1168.5634 | 1534.519 | 1781.7243
10.9 | [5 empty] | 482.5681 | 619.8926 | 763.2657 | 1113.3784 | 1171.6514 | 1546.0103 | 1785.3057
11 | [5 empty] | 486.2331 | 623.9933 | 764.8005 | 1122.8325 | 1174.7395 | 1557.5015 | 1788.8871
11.1 | [5 empty] | 488.0484 | 629.5048 | 769.3564 | 1136.1469 | 1184.2658 | 1559.6441 | 1802.1741
11.2 | [5 empty] | 489.8638 | 635.0162 | 773.9124 | 1149.4613 | 1193.7922 | 1561.7868 | 1815.461
11.3 | [5 empty] | 491.6792 | 640.5277 | 778.4683 | 1162.7757 | 1203.3185 | 1563.9294 | 1828.748
11.4 | [5 empty] | 493.4945 | 646.0392 | 783.0242 | 1176.0901 | 1212.8448 | 1566.072 | 1842.0349
11.5 | [5 empty] | 495.3099 | 651.5507 | 787.5801 | 1189.4045 | 1222.3712 | 1568.2146 | 1855.3219
11.6 | [5 empty] | 497.1253 | 657.0622 | 792.1361 | 1202.7189 | 1231.8975 | 1570.3572 | 1868.6088
11.7 | [5 empty] | 498.9406 | 662.5736 | 796.692 | 1216.0333 | 1241.4239 | 1572.4998 | 1881.8958
11.8 | [5 empty] | 500.756 | 668.0851 | 801.2479 | 1229.3477 | 1250.9502 | 1574.6424 | 1895.1827
11.9 | [5 empty] | 502.5713 | 673.5966 | 805.8038 | 1242.6621 | 1260.4766 | 1576.785 | 1908.4697
12 | [5 empty] | 504.3867 | 679.1081 | 810.3598 | 1255.9765 | 1270.0029 | 1578.9277 | 1921.7566
12.1 | [6 empty] | 684.6006 | 818.197 | 1267.2721 | 1283.2481 | 1580.2658 | 1941.1449
12.2 | [6 empty] | 690.0932 | 826.0342 | 1278.5677 | 1296.4934 | 1581.604 | 1960.5332
12.3 | [6 empty] | 695.5858 | 833.8714 | 1289.8632 | 1309.7386 | 1582.9422 | 1979.9216
12.4 | [6 empty] | 701.0784 | 841.7086 | 1301.1588 | 1322.9838 | 1584.2804 | 1999.3099
12.5 | [6 empty] | 706.571 | 849.5458 | 1312.4543 | 1336.229 | 1585.6186 | 2018.6982
12.6 | [6 empty] | 712.0635 | 857.383 | 1323.7499 | 1349.4742 | 1586.9568 | 2038.0865
12.7 | [6 empty] | 717.5561 | 865.2202 | 1335.0454 | 1362.7195 | 1588.295 | 2057.4749
12.8 | [6 empty] | 723.0487 | 873.0574 | 1346.341 | 1375.9647 | 1589.6332 | 2076.8632
12.9 | [6 empty] | 728.5413 | 880.8946 | 1357.6365 | 1389.2099 | 1590.9714 | 2096.2515
13 | [6 empty] | 734.0338 | 888.7318 | 1368.9321 | 1402.4551 | 1592.3095 | 2115.6398
13.1 | [6 empty] | 739.8721 | 897.2577 | 1376.847 | 1415.4352 | 1606.5187 | 2134.6828
13.2 | [6 empty] | 745.7103 | 905.7836 | 1384.7619 | 1428.4153 | 1620.7279 | 2153.7257
13.3 | [6 empty] | 751.5485 | 914.3095 | 1392.6768 | 1441.3954 | 1634.9371 | 2172.7686
13.4 | [6 empty] | 757.3867 | 922.8354 | 1400.5917 | 1454.3755 | 1649.1463 | 2191.8116
13.5 | [6 empty] | 763.2249 | 931.3613 | 1408.5066 | 1467.3556 | 1663.3555 | 2210.8545
13.6 | [6 empty] | 769.0631 | 939.8872 | 1416.4215 | 1480.3357 | 1677.5647 | 2229.8975
13.7 | [6 empty] | 774.9013 | 948.4131 | 1424.3363 | 1493.3158 | 1691.7739 | 2248.9404
13.8 | [6 empty] | 780.7395 | 956.939 | 1432.2512 | 1506.2959 | 1705.9831 | 2267.9833
13.9 | [6 empty] | 786.5777 | 965.4649 | 1440.1661 | 1519.276 | 1720.1923 | 2287.0263
14 | [6 empty] | 792.4159 | 973.9908 | 1448.081 | 1532.2561 | 1734.4015 | 2306.0692
14.1 | [6 empty] | 797.5109 | 981.0185 | 1460.338 | 1545.6621 | 1741.3878 | 2325.8085
14.2 | [6 empty] | 802.606 | 988.0463 | 1472.595 | 1559.0682 | 1748.374 | 2345.5479
14.3 | [6 empty] | 807.701 | 995.0741 | 1484.8521 | 1572.4742 | 1755.3602 | 2365.2872
14.4 | [6 empty] | 812.7961 | 1002.1018 | 1497.1091 | 1585.8802 | 1762.3464 | 2385.0265
14.5 | [6 empty] | 817.8912 | 1009.1296 | 1509.3661 | 1599.2863 | 1769.3327 | 2404.7659
14.6 | [6 empty] | 822.9862 | 1016.1573 | 1521.6231 | 1612.6923 | 1776.3189 | 2424.5052
14.7 | [6 empty] | 828.0813 | 1023.1851 | 1533.8801 | 1626.0983 | 1783.3051 | 2444.2445
14.8 | [6 empty] | 833.1763 | 1030.2128 | 1546.1371 | 1639.5044 | 1790.2913 | 2463.9839
14.9 | [6 empty] | 838.2714 | 1037.2406 | 1558.3941 | 1652.9104 | 1797.2776 | 2483.7232
15 | [6 empty] | 843.3664 | 1044.2684 | 1570.6511 | 1666.3164 | 1804.2638 | 2503.4625
15.1 | [6 empty] | 850.2026 | 1049.7194 | 1583.2076 | 1678.5452 | 1820.7239 | 2525.4659
15.2 | [6 empty] | 857.0387 | 1055.1705 | 1595.764 | 1690.7739 | 1837.1841 | 2547.4694
15.3 | [6 empty] | 863.8749 | 1060.6216 | 1608.3204 | 1703.0027 | 1853.6442 | 2569.4728
15.4 | [6 empty] | 870.711 | 1066.0727 | 1620.8769 | 1715.2314 | 1870.1044 | 2591.4762
15.5 | [6 empty] | 877.5472 | 1071.5238 | 1633.4333 | 1727.4602 | 1886.5645 | 2613.4796
15.6 | [6 empty] | 884.3833 | 1076.9748 | 1645.9897 | 1739.689 | 1903.0246 | 2635.483
15.7 | [6 empty] | 891.2195 | 1082.4259 | 1658.5462 | 1751.9177 | 1919.4848 | 2657.4864
15.8 | [6 empty] | 898.0556 | 1087.877 | 1671.1026 | 1764.1465 | 1935.9449 | 2679.4899
15.9 | [6 empty] | 904.8918 | 1093.3281 | 1683.659 | 1776.3752 | 1952.4051 | 2701.4933
16 | [6 empty] | 911.728 | 1098.7792 | 1696.2155 | 1788.604 | 1968.8652 | 2723.4967
16.1 | [8 empty] | 1709.8092 | 1803.3003 | 1985.9806 | 2743.528
16.2 | [8 empty] | 1723.403 | 1817.9967 | 2003.096 | 2763.5593
16.3 | [8 empty] | 1736.9967 | 1832.6931 | 2020.2114 | 2783.5907
16.4 | [8 empty] | 1750.5905 | 1847.3894 | 2037.3268 | 2803.622
16.5 | [8 empty] | 1764.1842 | 1862.0858 | 2054.4422 | 2823.6533
16.6 | [8 empty] | 1777.778 | 1876.7822 | 2071.5576 | 2843.6847
16.7 | [8 empty] | 1791.3717 | 1891.4785 | 2088.673 | 2863.716
16.8 | [8 empty] | 1804.9655 | 1906.1749 | 2105.7884 | 2883.7473
16.9 | [8 empty] | 1818.5593 | 1920.8712 | 2122.9038 | 2903.7786
17 | [8 empty] | 1832.153 | 1935.5676 | 2140.0192 | 2923.81
17.1 | [8 empty] | 1842.4906 | 1951.0868 | 2158.2217 | 2945.2512
17.2 | [8 empty] | 1852.8283 | 1966.6061 | 2176.4243 | 2966.6924
17.3 | [8 empty] | 1863.1659 | 1982.1253 | 2194.6268 | 2988.1336
17.4 | [8 empty] | 1873.5035 | 1997.6446 | 2212.8294 | 3009.5748
17.5 | [8 empty] | 1883.8411 | 2013.1638 | 2231.0319 | 3031.016
17.6 | [8 empty] | 1894.1787 | 2028.6831 | 2249.2345 | 3052.4572
17.7 | [8 empty] | 1904.5164 | 2044.2023 | 2267.4371 | 3073.8984
17.8 | [8 empty] | 1914.854 | 2059.7216 | 2285.6396 | 3095.3396
17.9 | [8 empty] | 1925.1916 | 2075.2408 | 2303.8422 | 3116.7809
18 | [8 empty] | 1935.5292 | 2090.76 | 2322.0447 | 3138.2221
18.1 | [8 empty] | 1950.4586 | 2100.5995 | 2342.4704 | 3162.5092
18.2 | [8 empty] | 1965.388 | 2110.4389 | 2362.8961 | 3186.7963
18.3 | [8 empty] | 1980.3174 | 2120.2783 | 2383.3218 | 3211.0834
18.4 | [8 empty] | 1995.2468 | 2130.1177 | 2403.7474 | 3235.3706
18.5 | [8 empty] | 2010.1762 | 2139.9571 | 2424.1731 | 3259.6577
18.6 | [8 empty] | 2025.1056 | 2149.7965 | 2444.5988 | 3283.9448
18.7 | [8 empty] | 2040.035 | 2159.6359 | 2465.0245 | 3308.2319
18.8 | [8 empty] | 2054.9644 | 2169.4754 | 2485.4502 | 3332.519
18.9 | [8 empty] | 2069.8939 | 2179.3148 | 2505.8759 | 3356.8062
19 | [8 empty] | 2084.8233 | 2189.1542 | 2526.3015 | 3381.0933