## Slide 1
Introduction
Frese Delta T
Introduction 2017

## Slide 2
Introduction
Frese Delta T

## Slide 3
Frese Delta T is a supply and return temperature controller with two temperature sensors. Frese Delta T limits the flow through the terminal unit by means of a control valve in order to obtain the minimum required (designed) temperature difference in the supply and return lines of the system and thus enhance it’s efficiency and optimize pump energy consumption.
Introduction
Frese Delta T
What is Frese Delta T ?

## Slide 4
In a typical cooling system the supply water temperature may be 6oC and return 12oC. That means the desired DT is 12-6 = 6oC. If the DT decreases to 3oC, the flow increases by a 100%!!! The same happens in heating systems though the temperatures are of course higher.
DT
Design flow pre-set on the valve
If the flow is too high compared to the load, the temperature difference is too low
At too high flow the efficiency of the system decreases
DT syndrom
Frese Delta T

## Slide 5
If the DT is TOO low compared to what the system has been sized for, the pump operates at TOO high speed and provides TOO much flow using TOO much energy, producing too much noise due to higher pressure loss.
System pump with required DT:
Pump is not oversized
Low Energy consumption
Low running cost
System pump with TOO low DT:
Too much flow
Too high speed
Too much noise
Too much energy
Too high running cost
Too low system efficiency
DT is temperature difference between the supply and return line
DT
DT syndrom
Frese Delta T

## Slide 6
Frese DELTA T consists of:
Controller
Two temperature sensors
Straps for fastening the temperature sensors on pipes up to DN300
Controller
Temperature sensors
The design
Frese Delta T

## Slide 7
The temperature sensor 1 is always used as a reference.
Based on the detected temperature by the sensor 1 the controller determines whether the system operates in cooling or heating mode.
The temperature sensor 2 is used to measure the return water temperature and based on this the controller calculates the DT.
Temperature sensor 2
Temperature sensor 1
Functionality
Frese Delta T
It is not important to know which temperature sensors is NO 1 and which NO 2 (they can be swapped). The control box detects this automatically!

## Slide 8
When the measured DT is lower compared to the set DT the controller sends signal to the picv (or two way valve) to decrease the flow.
If the measured DT is equal or higher than the set DT the controller takes no action. The flow is 100% controlled by the external control signal.
Controller
Two way or picv valve
Functionality
Frese Delta T

## Slide 9
To avoid starving the coil of flow the Frese Delta T Control System is programmed so it never sends a signal to the actuator of less than 1.5 V. This means that the DELTA T Control System does not close the valve fully even if the measured ΔT is below the set point. The BMS can always close the valve if the signal sent is less than 1.5V.
Min signal 1,5V
Functionality
Frese Delta T

## Slide 10
To set ΔT, button OK (2) should be pressed and held for minimum one second. The set point ΔT value is changed by the buttons (1) and confirmed by the OK button (2)
The display (3) will change between the actual ΔT value and the set point ΔT value. When the set point ΔT is displayed, the green LED (4) will be on. The controller auto-detects and indicates with the red or blue LED (5) whether it operates in heating or cooling systems.
Functionality
Frese Delta T
Setting of DT

## Slide 11
The external control signal of 0-10V (for controlling the actuator) is provided from an external controller to the Frese Delta T control box. The Frese Delta T control box uses 24V power supply and can control a 24V actuator with 0-10V signal. The temperature in the pipe changes the rezistance of the sensors (connected to the Frese Delta T control box) which is converted by the Frese Delta T controll box into temperature reading.
Functionality
Frese Delta T
Wiring

## Slide 12
The Frese Delta T control box can be mounted using DIN rail clips or directly on a wall.
The temperature sensors can be mounted on a pipe using cable ties.
Functionality
Frese Delta T
Mounting on a wall
Mounting with DIN rail clips
Mounting temperature sensors with cable ties

## Slide 13
The controller uses 0-10 V signal to communicate with the actuator and 0-10V signal to communicate with the BMS system.
Controller data
Technical data
Frese Delta T

## Slide 14
The controller must be installed at each terminal unit where flow is controlled by a motorized valve.
One controller can operate one valve.
Frese DELTA T can be used in plant rooms or at air handling units to control single circuits.
Where to install?
Application
Frese Delta T

## Slide 15
Frese DELTA T can be used in branches with several terminal units controlled by one motorized valve.
Where to install?
Application
Frese Delta T
One room (area) in the building

## Slide 16
Solves low DT syndrome
Saves pump energy typically more than 50%
Releases additional system capacity
Simple to use in existing and new system
Plug and „play”
Helps to avoid noise in the system caused by too high flow
Increases system efficiency
Benefits
Frese Delta T
Reduces maintenance cost
Increases chiller efficiency

## Slide 17
Established in 1960, DTU’s main campus located north of Copenhagen near the town of Lyngby, consists of more than 100 buildings and covers an area of 106 hectares. With approximately 9,000 students and 5,500 staff, DTU is currently (2017) investing more than DKK 4 billion in its campus development to create optimum conditions for research and education with state-of-the-art facilities.
Case study at DTU
The University was founded in 1829 and today is among the top universities in the world and is ranked No. 1 in the Nordic region on the 2011/2012 Leiden Ranking of 500 major universities.
Case study
Frese Delta T

## Slide 18
As more buildings have been added to the campus over the years, the capacity of the cooling network has not been developed to meet the extra demand. Consequently, the cooling capacity of the current system has now reached its limit. DTU have been considering a number of options to try and increase the capacity of the cooling system, including upgrading and upsizing the distribution pipework.
The DTU Lyngby campus, which consists of more than 100 buildings and covers an area of 106 hectares, is served by a district cooling network providing cooling for laboratories, data centers and classrooms.
Case study
Frese Delta T

## Slide 19
During investigation, poor DT’s within the system were identified as part of the capacity problem. The district cooling system has a design DT of 6°C, but many buildings were found to be running with an actual DT of between 1°C and 3°C.
Case study
Frese Delta T

## Slide 20
A laboratory building was selected as the test site for the Frese DELTA T Control System and within this building, the freezer room which houses multiple -80°C freezers. The freezers expel large amounts of heat in to the room and the room temperature is controlled by two fan coil units.
Initially, the water flow to the fan coil units was controlled by a DN15 static 2-way control valve and 0-10V modulating actuator.
The room temperature is stable at 21°C
Case study
Frese Delta T

## Slide 21
Part 1: Static 2-way control valve and 0-10V modulating actu-ator, without Frese Delta T Control
Part 2: Static 2-way control valve and 0-10V modulating actuator, with Frese Delta T Control
Case study
Frese Delta T

## Slide 22
Part 1: Static 2-way control valve and 0-10V modulating actuator, without Delta T Control
Initially, the water flow to the fan coil units was controlled by a DN15 static 2-way control valve and 0-10V modulating actuator.
The room temperature is stable at 21°C
Part 2: Static 2-way control valve and 0-10V modulating actuator, with Delta T Control
Case study
Frese Delta T

## Slide 23
Part 1: Static 2-way control valve and 0-10V modulating actuator, without Delta T Control
The Delta T Control System was used to measure and monitor, for a period of one week, the current Delta T being achieved with the original installation setup. The Frese Delta T Control System can be used as a diagnostic tool, as well as a control system, to collect and analyze data from existing systems.
Part 2: Static 2-way control valve and 0-10V modulating actuator, with Delta T Control
Case study
Frese Delta T

## Slide 24
Part 1: Static 2-way control valve and 0-10V modulating actuator, without Delta T Control
In this part of the study there is no control of the DT. The control box monitors both the BMS control signal and the flow and return water temperatures to and from the fan coil.
Part 2: Static 2-way control valve and 0-10V modulating actuator, with Delta T Control
Case study
Frese Delta T

## Slide 25
Part 1: Static 2-way control valve and 0-10V modulating actuator, without Delta T Control.
Room temperature was stable at 21°C.
Average measured DT, over the 1 week period, was 3.1°C versus a setpoint of 5.0°C.
Actual measured flow from the coil was 1.60 m3/h (0.44 l/s).
Part 2: Static 2-way control valve and 0-10V modulating actuator, with Delta T Control
Grey: BMS signal to control box (0-10VDC)
Orange: DT setpoint 5.0°C
Blue: Actual measured DT
Yellow: Frese Delta T signal to valve actuator (zero signal as monitoring only)
Cooling Demand ~ 5.7 kW
Case study
Frese Delta T

## Slide 26
Static 2-way control valve and 0-10V modulating actuator, with DT Control
Part 2: Static 2-way control valve and 0-10V modulating actuator, with DT Control
Case study
Frese Delta T

## Slide 27
Room temperature was stable at 21°C.
Average measured DT, over the 1 week period, was 5.1°C versus a setpoint of 5.0°C.
Actual measured flow from the coil was 0.986 m3/h (0.27 l/s)
Part 2: Static 2-way control valve and 0-10V modulating actuator, with Delta T Control
Grey: BMS signal to control box (0-10VDC)
Orange: DT setpoint 5.0°C
Blue: Actual measured DT
Yellow: Frese Delta T control box signal to valve actuator (0-10V)
Cooling Demand ~ 5.7 kW
Part 2: Static 2-way control valve and 0-10V modulating actuator, with DT Control
Case study
Frese Delta T

## Slide 28
Case study
Frese Delta T
The average flow is lower
The Coil DT is higher

## Slide 29
When fitted with a Static 2-Way Control Valve and Frese DT Control, the same FCU can satisfy the same cooling load with 77% less pump energy consumption compared with when controlled by a Static 2-Way Control Valve only.
E% saving = 77%
Case study
Frese Delta T

## Slide 30
Comparison of:
2 way control valve
Vs
2 way control valve with Frese Delta T
Case study
Frese Delta T
2 way control valve Vs 2-way control valve with Frese Delta T:
2-way control valve, cooling capacity 5.6kW, flow 1600l/h, DT=3oC, pump energy 100%
2-way control valve with Frese Delta T, cooling capacity 5.6kW, flow 980l/h, DT=5oC, pump energy 23%.
Chart: 
 | 100 | 3 | 0 | 100 | 5 | 77
No Frese Delta T
With Frese Delta T
E% saving = 77%

## Slide 31
Case study
Frese Delta T
2 way control valve Vs PICV (no Frese Delta T):
2-way control valve, flow 1600l/h, DT=2.8oC,
PICV, flow 1100l/h, DT=4.1oC,
Pump energy saving 67%
Comparison of:
2 way control valve
Vs
PICV
E% saving = 67%

## Slide 32
PICV with Frese Delta T
Case study
Frese Delta T
All the tests have been carried out at DTU – Technical University and the test results indicate that the greatest saving in energy has been recorded when Frese Delta T had controlled a picv valve – Frese Optima Compact.

## Slide 33
Where and how to use Frese Delta T?
New buildings?
Retrofit?
Contractor?
Building owner?
Facility manager
Installer?
DELTA T Vs BMS? DELTA T Vs PICV?
DELTA T Vs nothing?
...
...
Diagnostic box?
Way to the market
Frese Delta T
There may be different ways to the market depending on the situation in the market in question.
There is at the moment no device in the market capable of providing the same functionality on any motorized valve.
Frese can also offer the diagnostic box to collect and process data for the customer.

## Slide 34
One of suggested ways to the market:
Way to the market
Frese Delta T
Next best alternative | Audience/Route to Market | Situation(s)
BMS | Consultant | New build
PICV | Contractor | Retrofit
Belimo Energy Valve | Owner | Problematic building
Do nothing | Facilities Management | 
If the customer experiences DT issues, it should be possible to take direct contact to the building owner or the facility management.
The existing and causing problems buildings should be in the focus of attention.
The diagnostic box can be used to prove that the DT problem persists and Frese Delta T, perhaps along with some picv valves, can help.

## Slide 35
Another suggested way to the market:
Way to the market
Frese Delta T
Next best alternative | Audience/Route to Market | Situation(s)
BMS | Consultant | New build
PICV | Contractor | Retrofit
Belimo Energy Valve | Owner | Problematic building
Do nothing | Facilities Management | 
If the customer experiences DT issues, it should be possible to take contact to a consultant who can advise the customer on the course of action.
The existing and causing problems buildings should be in the focus of attention.
The diagnostic box can be used to prove that the DT problem persists and Frese Delta T, perhaps along with some picv, valves can help .

## Slide 36
Discussion
Frese Delta T
Any questions?

## Slide 37
Contact
Frese Delta T
In case of questions please contact product manager:
Thank you 